## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-01-01
System Name: | Cascade Gorge Properties |  |  | ID#: 91556 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 | 25 | 0.05 | 0.05
2 | 46 | 44 | 2 | 25 | 0.05 | 0.05
3 | 46 | 44 | 2 | 25 | 0.05 | 0.05
4 | 46 | 44 | 2 | 25 | 0.05 | 0.05
5 | 46 | 44 | 2 | 25 | 0.05 | 0.05
6 | 46 | 44 | 2 | 25 | 0.05 | 0.05
7 | 46 | 44 | 2 | 25 | 0.05 | 0.05
8 | 46 | 44 | 2 | 25 | 0.05 | 0.05
9 | 46 | 44 | 2 | 25 | 0.05 | 0.05
10 | 46 | 44 | 2 | 25 | 0.05 | 0.05
11 | 46 | 44 | 2 | 25 | 0.05 | 0.05
12 | 46 | 44 | 2 | 25 | 0.05 | 0.05
13 | 46 | 44 | 2 | 25 | 0.05 | 0.05
14 | 46 | 44 | 2 | 25 | 0.05 | 0.05
15 | 46 | 44 | 2 | 25 | 0.05 | 0.05
16 | 46 | 44 | 2 | 25 | 0.05 | 0.05
17 | 46 | 44 | 2 | 25 | 0.05 | 0.05
18 | 46 | 44 | 2 | 25 | 0.5 | 0.05
19 | 46 | 44 | 2 | 25 | 0.05 | 0.05
20 | 46 | 44 | 2 | 25 | 0.05 | 0.05
21 | 46 | 44 | 2 | 25 | 0.05 | 0.05
22 | 46 | 44 | 2 | 25 | 0.05 | 0.05
23 | 46 | 44 | 2 | 25 | 0.046 | 0.05
24 | 46 | 44 | 2 | 25 | 0.05 | 0.05
25 | 46 | 44 | 2 | 25 | 0.047 | 0.047
26 | 46 | 44 | 2 | 25 | 0.05 | 0.05
27 | 46 | 44 | 2 | 25 | 0.047 | 0.047
28 | 46 | 44 | 2 | 25 | 0.05 | 0.05
29 | 46 | 44 | 2 | 25 | 0.046 | 0.046
30 | 46 | 44 | 2 | 25 | 0.05 | 0.05
31 | 46 | 44 | 2 | 25 | 0.05 | 0.05
Cartridge & Bag Filtration
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | YES
Notes: PSI = pounds per square inch |  |  |  |  | Cedar Hursh
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | CT's met everyday? (see back) |  | 2024-01-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. | [6 empty] | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2024-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T)Contact Time (T)Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2CT Met? 2CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.8 | 207 | 579.6 | 8.8 | 7.8 | 68.3425 | Yes | 2.5
2 | 3 | 207 | 621 | 8.5 | 7.8 | 71.4206 | Yes | 2.5
3 | 2.8 | 207 | 579.6 | 8.5 | 7.7 | 67.2619 | Yes | 2.5
4 | 2.8 | 207 | 579.6 | 8.4 | 7.7 | 67.7237 | YES | 2.5
5 | 2.5 | 207 | 517.5 | 7.3 | 7.8 | 73.1282 | YES | 2.5
6 | 3 | 207 | 621 | 6.6 | 7.6 | 75.6392 | YES | 2.5
7 | 2.8 | 207 | 579.6 | 6.7 | 7.6 | 73.3698 | YES | 2.5
8 | 2.5 | 207 | 517.5 | 6.6 | 7.6 | 71.3132 | YES | 2.5
9 | 2.4 | 207 | 496.8 | 6.7 | 7.5 | 67.4892 | YES | 2.5
10 | 2.5 | 207 | 517.5 | 6.1 | 7.8 | 79.4352 | YES | 2.5
11 | 2.5 | 207 | 517.5 | 6 | 7.7 | 77.0961 | YES | 2.5
12 | 2.5 | 207 | 517.5 | 5.9 | 7.7 | 77.63 | YES | 2.5
13 | 2.8 | 207 | 579.6 | 5.8 | 7.6 | 78.0643 | YES | 2.5
14 | 2.7 | 207 | 558.9 | 5.9 | 7.6 | 76.6169 | YES | 2.5
15 | 2.9 | 207 | 600.3 | 6.1 | 7.6 | 77.3735 | YES | 2.5
16 | 2.8 | 207 | 579.6 | 6 | 7.6 | 76.9942 | YES | 2.5
17 | 2.4 | 207 | 496.8 | 6.4 | 7.5 | 68.8897 | YES | 2.5
18 | 2.4 | 207 | 496.8 | 6.2 | 7.6 | 72.4428 | YES | 2.5
19 | 2.5 | 207 | 517.5 | 7.5 | 7.6 | 67.048 | YES | 2.5
20 | 2.1 | 207 | 434.7 | 6.9 | 8 | 77.169 | YES | 2.5
21 | 2.3 | 207 | 476.1 | 6.7 | 7.9 | 77.2201 | YES | 2.5
22 | 2.5 | 207 | 517.5 | 8.4 | 7.7 | 65.3871 | YES | 2.5
23 | 2.2 | 207 | 455.4 | 8 | 7.4 | 58.2019 | YES | 2.5
24 | 2.3 | 207 | 476.1 | 8.1 | 7.5 | 60.6349 | YES | 2.5
25 | 2.1 | 207 | 434.7 | 8 | 7.5 | 59.6455 | YES | 2.5
26 | 2 | 207 | 414 | 8.2 | 7.5 | 58.1641 | YES | 2.5
27 | 2.2 | 207 | 455.4 | 8.7 | 7.5 | 57.5475 | YES | 2.5
28 | 1.8 | 207 | 372.6 | 9.9 | 7.5 | 50.6945 | YES | 2.5
29 | 2 | 207 | 414 | 9.7 | 7.5 | 52.571 | YES | 2.5
30 | 2.2 | 207 | 455.4 | 10.4 | 7.5 | 51.3259 | YES | 2.5
31 | 2.3 | 207 | 476.1 | 9.8 | 7.5 | 54.053 | YES | 2.5
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2