## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-03-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 |  | 0.046 | 0.05
2 | 46 | 44 | 2 |  | 0.046 | 0.05
3 | 46 | 44 | 2 |  | 0.045 | 0.05
4 | 46 | 44 | 2 |  | 0.045 | 0.05
5 | 46 | 44 | 2 |  | 0.05 | 0.05
6 | 46 | 44 | 2 |  | 0.05 | 0.05
7 | 46 | 44 | 2 |  | 0.05 | 0.05
8 | 46 | 44 | 2 |  | 0.05 | 0.05
9 | 46 | 44 | 2 |  | 0.05 | 0.05
10 | 46 | 44 | 2 |  | 0.05 | 0.05
11 | 46 | 44 | 2 |  | 0.05 | 0.05
12 | 46 | 44 | 2 |  | 0.05 | 0.05
13 | 46 | 44 | 2 |  | 0.05 | 0.05
14 | 46 | 44 | 2 |  | 0.05 | 0.05
15 | 46 | 44 | 2 |  | 0.05 | 0.05
16 | 46 | 44 | 2 |  | 0.05 | 0.05
17 | 46 | 44 | 2 |  | 0.05 | 0.05
18 | 46 | 44 | 2 |  | 0.05 | 0.05
19 | 46 | 44 | 2 |  | 0.05 | 0.05
20 | 46 | 44 | 2 |  | 0.05 | 0.05
21 | 46 | 44 | 2 |  | 0.05 | 0.05
22 | 46 | 44 | 2 |  | 0.05 | 0.05
23 | 46 | 44 | 2 |  | 0.05 | 0.05
24 | 46 | 44 | 2 |  | 0.05 | 0.05
25 | 46 | 44 | 2 |  | 0.05 | 0.05
26 | 46 | 44 | 2 |  | 0.05 | 0.05
27 | 46 | 44 | 2 |  | 0.05 | 0.05
28 | 46 | 44 | 2 |  | 0.05 | 0.05
29 | 46 | 44 | 2 |  | 0.05 | 0.05
30 | 46 | 44 | 2 |  | 0.05 | 0.05
31 | 46 | 44 | 2 |  | 0.05 | 0.05
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 4/03/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 287-2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2024-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.9 | 207 | 600.3 | 7.2 | 7.7 | 74.4076 | YES | 2.5
2 | 3.1 | 207 | 641.7 | 5.9 | 7.7 | 83.346 | YES | 2.5
3 | 3 | 207 | 621 | 5.1 | 7.7 | 87.0617 | YES | 2.5
4 | 2 | 207 | 414 | 4.6 | 7.8 | 83.0539 | YES | 2.5
5 | 2.1 | 207 | 434.7 | 4.1 | 7.8 | 87.012 | YES | 2.5
2.8 | 2.4 | 207 | 496.8 | 5.2 | 7.7 | 80.5183 | YES | 2.5
7 | 3 | 207 | 621 | 6.7 | 7.6 | 75.1199 | YES | 2.5
8 | 2.8 | 207 | 579.6 | 6.2 | 7.7 | 78.7838 | YES | 2.5
9 | 2.7 | 207 | 558.9 | 6 | 7.7 | 78.9406 | YES | 2.5
10 | 2.9 | 207 | 600.3 | 6.3 | 7.7 | 79.1725 | YES | 2.5
11 | 3 | 207 | 621 | 6.2 | 7.7 | 80.671 | YES | 2.5
12 | 3.1 | 207 | 641.7 | 7.1 | 7.7 | 76.711 | YES | 2.5
13 | 3.2 | 207 | 662.4 | 6.6 | 7.5 | 74.6536 | YES | 2.5
14 | 3.5 | 207 | 724.5 | 8.4 | 7.5 | 68.3425 | YES | 2.5
15 | 3.5 | 207 | 724.5 | 9.7 | 7.4 | 60.3144 | YES | 2.5
16 | 3.5 | 207 | 724.5 | 7.6 | 7.2 | 64.7121 | YES | 2.5
17 | 3.5 | 207 | 724.5 | 8.1 | 7 | 58.1803 | YES | 2.5
18 | 3.5 | 207 | 724.5 | 10 | 7.1 | 53.0568 | YES | 2.5
19 | 3.5 | 207 | 724.5 | 9.8 | 7.1 | 53.7748 | YES | 2.5
20 | 3.5 | 207 | 724.5 | 9.9 | 7.3 | 57.3932 | YES | 2.5
21 | 3.5 | 207 | 724.5 | 9.7 | 7.2 | 56.1171 | YES | 2.5
22 | 3.5 | 207 | 724.5 | 9.2 | 7.2 | 58.0456 | YES | 2.5
23 | 3.5 | 207 | 724.5 | 9 | 7.2 | 58.837 | YES | 2.5
24 | 3.5 | 207 | 724.5 | 9.9 | 7.3 | 57.3932 | YES | 2.5
25 | 3.5 | 207 | 724.5 | 9.7 | 7.3 | 58.1749 | YES | 2.5
26 | 3.5 | 207 | 724.5 | 9.9 | 7.3 | 57.3932 | YES | 2.5
27 | 3.5 | 207 | 724.5 | 9.8 | 7.3 | 57.7826 | YES | 2.5
28 | 3.5 | 207 | 724.5 | 9.9 | 7.3 | 57.3932 | YES | 2.5
29 | 2.5 | 207 | 517.5 | 9.6 | 7.3 | 52.1859 | YES | 2.5
30 | 3.5 | 207 | 724.5 | 9.6 | 7.4 | 60.7252 | YES | 2.5
31 | 3.5 | 207 | 724.5 | 9.7 | 7.4 | 60.3144 | YES | 2.5
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2