## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-04-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 |  | 0.05 | 0.05
2 | 46 | 44 | 2 |  | 0.05 | 0.05
3 | 45 | 43 | 2 |  | 0.017 | 0.017
4 | 0 | 0 | 0 |  | 0.316 | 0.316
5 | 0 | 0 | 0 |  | 0.016 | 0.02
6 | 0 | 0 | 0 |  | 0.016 | 0.02
7 | 0 | 0 | 0 |  | 0.016 | 0.02
8 | 45 | 43 | 2 |  | 0.019 | 0.02
9 | 45 | 43 | 2 |  | 0.017 | 0.02
10 | 45 | 43 | 2 |  | 0.02 | 0.02
11 | 0 | 0 | 0 |  | 0.02 | 0.02
12 | 0 | 0 | 0 |  | 0.02 | 0.02
13 | 0 | 0 | 0 |  | 0.02 | 0.02
14 | 0 | 0 | 0 |  | 0.02 | 0.02
15 | 45 | 43 | 2 |  | 0.02 | 0.02
16 | 0 | 0 | 0 |  | 0.02 | 0.02
17 | 45 | 43 | 2 |  | 0.02 | 0.02
18 | 0 | 0 | 0 |  | 0.02 | 0.02
19 | 45 | 43 | 2 |  | 0.02 | 0.02
20 | 0 | 0 | 0 |  | 0.02 | 0.02
21 | 0 | 0 | 0 |  | 0.02 | 0.02
22 | 0 | 0 | 0 |  | 0.02 | 0.02
23 | 0 | 0 | 0 |  | 0.03 | 0.03
24 | 0 | 0 | 0 |  | 0.02 | 0.02
25 | 0 | 0 | 0 |  | 0.02 | 0.02
26 | 0 | 0 | 0 |  | 0.132 | 0.13
27 | 0 | 0 | 0 |  | 0.02 | 0.02
28 | 0 | 0 | 0 |  | 0.02 | 0.02
29 | 45 | 43 | 2 |  | 0.02 | 0.02
30 | 45 | 43 | 2 |  | 0.02 | 0.02
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 5/3/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2024-04-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.5 | 207 | 724.5 | 10.1 | 7.3 | 56.6227 | YES | 2.5
2 | 3.5 | 207 | 724.5 | 10.2 | 7.3 | 56.2417 | YES | 2.5
3 | 3.5 | 207 | 724.5 | 10.1 | 7.4 | 58.7006 | YES | 3
4 | 3.5 | 207 | 724.5 | 9 | 7.4 | 63.2544 | YES | 0
5 | 3.5 | 207 | 724.5 | 9.2 | 7.4 | 62.399 | YES | 0
6 | 3.5 | 207 | 724.5 | 9.2 | 7.4 | 62.399 | YES | 0
7 | 3.5 | 207 | 724.5 | 9.1 | 7.4 | 62.8251 | YES | 0
8 | 3.5 | 207 | 724.5 | 9.2 | 7.4 | 62.399 | YES | 2.5
9 | 3.5 | 207 | 724.5 | 11.4 | 7.4 | 53.7698 | YES | 2.5
10 | 3.5 | 207 | 724.5 | 13.9 | 7.4 | 45.1323 | YES | 2.5
11 | 3.5 | 207 | 724.5 | 13.5 | 7.4 | 46.3427 | YES | 0
12 | 3.5 | 207 | 724.5 | 11.3 | 7.2 | 50.3981 | YES | 0
13 | 3.5 | 207 | 724.5 | 11.7 | 7.4 | 52.6969 | YES | 0
14 | 3.5 | 207 | 724.5 | 11.5 | 7.4 | 53.4095 | YES | 0
15 | 3.5 | 207 | 724.5 | 11.5 | 7.6 | 57.3878 | YES | 2.5
16 | 3.5 | 207 | 724.5 | 11.3 | 7.6 | 58.1695 | YES | 0
17 | 3.5 | 207 | 724.5 | 11 | 7.3 | 53.2917 | YES | 2.5
18 | 3.5 | 207 | 724.5 | 11.8 | 7.3 | 50.509 | YES | 0
19 | 3.5 | 207 | 724.5 | 13.9 | 7.4 | 45.1323 | YES | 2.5
20 | 2.8 | 207 | 579.6 | 15.1 | 7.5 | 39.9528 | YES | 0
21 | 2.7 | 207 | 558.9 | 15 | 7.5 | 39.7657 | YES | 0
22 | 3.2 | 207 | 662.4 | 12.9 | 7.4 | 46.6122 | YES | 0
23 | 3 | 207 | 621 | 12.7 | 7.4 | 46.1779 | YES | 0
24 | 3 | 207 | 621 | 12.6 | 7.4 | 46.4844 | YES | 0
25 | 2.8 | 207 | 579.6 | 12.5 | 7.4 | 45.7475 | YES | 0
26 | 3 | 207 | 621 | 13 | 7.4 | 45.2704 | YES | 0
27 | 3.2 | 207 | 662.4 | 12.8 | 7.4 | 46.9215 | YES | 0
28 | 3.3 | 207 | 683.1 | 11.1 | 7.4 | 53.6165 | YES | 0
29 | 3.1 | 207 | 641.7 | 11.6 | 7.4 | 50.6712 | YES | 2.5
30 | 2.2 | 207 | 455.4 | 11.1 | 7.5 | 48.9801 | YES | 2.5
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2