## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-06-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 |  | 0.025 | 0.03
2 | 0 | 0 | 0 |  | 0.024 | 0.02
3 | 0 | 0 | 0 |  | 0.025 | 0.03
4 | 0 | 0 | 0 |  | 0.024 | 0.02
5 | 0 | 0 | 0 |  | 0.024 | 0.02
6 | 46 | 44 | 2 |  | 0.025 | 0.03
7 | 46 | 44 | 2 |  | 0.025 | 0.03
8 | 46 | 44 | 2 |  | 0.024 | 0.02
9 | 0 | 0 | 0 |  | 0.07 | 0.07
10 | 46 | 44 | 2 |  | 0.025 | 0.03
11 | 46 | 44 | 2 |  | 0.024 | 0.02
12 | 46 | 44 | 2 |  | 0.025 | 0.03
13 | 0 | 0 | 0 |  | 0.024 | 0.02
14 | 46 | 44 | 2 |  | 0.025 | 0.03
15 | 0 | 0 | 0 |  | 0.024 | 0.02
16 | 46 | 44 | 2 |  | 0.024 | 0.02
17 | 46 | 44 | 2 |  | 0.024 | 0.02
18 | 46 | 44 | 2 |  | 0.024 | 0.02
19 | 46 | 44 | 2 |  | 0.025 | 0.03
20 | 46 | 44 | 2 |  | 0.03 | 0.03
21 | 46 | 44 | 2 |  | 0.03 | 0.03
22 | 46 | 44 | 2 |  | 0.03 | 0.03
23 | 46 | 44 | 2 |  | 0.03 | 0.03
24 | 0 | 0 | 0 |  | 0.02 | 0.02
25 | 46 | 44 | 2 |  | 0.03 | 0.03
26 | 46 | 44 | 2 |  | 0.03 | 0.03
27 | 46 | 44 | 2 |  | 0.03 | 0.03
28 | 46 | 44 | 2 |  | 0.03 | 0.03
29 | 46 | 44 | 2 |  | 0.03 | 0.03
30 | 46 | 44 | 2 |  | 0.03 | 0.03
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:6/7/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2024-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.3 | 207 | 683.1 | 17.4 | 7.4 | 34.9793 | YES | 2.5
2 | 3.4 | 207 | 703.8 | 15.3 | 7.4 | 40.6725 | YES | 0
3 | 3.4 | 207 | 703.8 | 16.1 | 7.4 | 38.5703 | YES | 0
4 | 3.5 | 207 | 724.5 | 16.8 | 7.4 | 37.2384 | YES | 0
5 | 3.5 | 207 | 724.5 | 21.5 | 7.4 | 27.2207 | YES | 0
6 | 3.3 | 207 | 683.1 | 19.2 | 7.4 | 31.0269 | YES | 2.5
7 | 3.1 | 207 | 641.7 | 20 | 7.4 | 28.7497 | YES | 2.5
8 | 3.3 | 207 | 683.1 | 19.7 | 7.4 | 30.0087 | YES | 2.5
9 | 3.5 | 207 | 724.5 | 19.6 | 7.4 | 30.9062 | YES | 0
0.5 | 3.3 | 207 | 683.1 | 18.6 | 7.4 | 32.2934 | YES | 2.5
11 | 3.5 | 207 | 724.5 | 18.8 | 7.4 | 32.5994 | YES | 2.5
12 | 3.5 | 207 | 724.5 | 18.9 | 7.4 | 32.3829 | YES | 2.5
13 | 3.5 | 207 | 724.5 | 17.6 | 7.4 | 35.3101 | YES | 0
14 | 3.5 | 207 | 724.5 | 17.8 | 7.4 | 34.8435 | YES | 2.5
15 | 3.3 | 207 | 683.1 | 18 | 7.5 | 34.8756 | YES | 0
16 | 3.5 | 207 | 724.5 | 17.9 | 7.5 | 35.9148 | YES | 2.5
17 | 3.5 | 207 | 724.5 | 18.2 | 7.5 | 35.2055 | YES | 2.5
18 | 3.5 | 207 | 724.5 | 18.1 | 7.5 | 35.4404 | YES | 2.5
19 | 3.5 | 207 | 724.5 | 19.5 | 7.4 | 31.113 | YES | 2.5
20 | 3.5 | 207 | 724.5 | 19.8 | 7.4 | 30.4964 | YES | 2.5
21 | 3.4 | 207 | 703.8 | 19.9 | 7.4 | 29.9502 | YES | 2.5
22 | 2.9 | 207 | 600.3 | 19.9 | 7.4 | 28.2891 | YES | 2.5
23 | 3.1 | 207 | 641.7 | 20 | 7.4 | 28.7497 | YES | 2.5
24 | 3 | 207 | 621 | 20.1 | 7.4 | 28.2339 | YES | 0
25 | 3.1 | 207 | 641.7 | 19.6 | 7.4 | 29.5285 | YES | 2.5
26 | 3.2 | 207 | 662.4 | 19.7 | 7.4 | 29.6684 | YES | 2.5
27 | 3.5 | 207 | 724.5 | 20.2 | 7.4 | 29.6928 | YES | 2.5
28 | 3.5 | 207 | 724.5 | 19.7 | 7.4 | 30.7006 | YES | 2.5
29 | 3.5 | 207 | 724.5 | 19.9 | 7.4 | 30.2936 | YES | 2.5
30 | 3.5 | 207 | 724.5 | 20.1 | 7.4 | 29.8918 | YES | 2.5
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2