## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-07-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 |  | 0.03 | 0.03
2 | 46 | 44 | 2 |  | 0.03 | 0.03
3 | 46 | 44 | 2 |  | 0.03 | 0.03
4 | 46 | 44 | 2 |  | 0.03 | 0.03
5 | 0 | 0 | 0 |  | 0.03 | 0.03
6 | 46 | 44 | 2 |  | 0.03 | 0.03
7 | 46 | 44 | 2 |  | 0.03 | 0.03
8 | 46 | 44 | 2 |  | 0.03 | 0.03
9 | 46 | 44 | 2 |  | 0.03 | 0.03
10 | 0 | 0 | 0 |  | 0.03 | 0.03
11 | 46 | 44 | 2 |  | 0.03 | 0.03
12 | 46 | 44 | 2 |  | 0.03 | 0.03
13 | 46 | 44 | 2 |  | 0.03 | 0.03
14 | 46 | 44 | 2 |  | 0.03 | 0.03
15 | 46 | 44 | 2 |  | 0.03 | 0.03
16 | 46 | 44 | 2 |  | 0.03 | 0.03
17 | 46 | 44 | 2 |  | 0.03 | 0.03
18 | 46 | 44 | 2 |  | 0.025 | 0.03
19 | 46 | 44 | 2 |  | 0.03 | 0.03
20 | 0 | 0 | 0 |  | 0.03 | 0.03
21 | 46 | 44 | 2 |  | 0.03 | 0.03
22 | 0 | 0 | 0 |  | 0.03 | 0.03
23 | 46 | 44 | 2 |  | 0.026 | 0.03
24 | 46 | 44 | 2 |  | 0.026 | 0.03
25 | 46 | 44 | 2 |  | 0.026 | 0.03
26 | 46 | 44 | 2 |  | 0.027 | 0.03
27 | 0 | 0 | 0 |  | 0.026 | 0.03
28 | 46 | 44 | 2 |  | 0.03 | 0.03
29 | 46 | 44 | 2 |  | 0.03 | 0.03
30 | 0 | 0 | 0 |  | 0.03 | 0.03
31 | 0 | 0 | 0 |  | 0.03 | 0.03
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: August 2, 2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2024-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.5 | 207 | 724.5 | 19.9 | 7.4 | 30.2936 | YES | 2.5
2 | 3.3 | 207 | 683.1 | 20.2 | 7.4 | 29.023 | YES | 2.5
3 | 3.4 | 207 | 703.8 | 20.3 | 7.4 | 29.1605 | YES | 2.5
4 | 3.1 | 207 | 641.7 | 22.4 | 7.4 | 24.4792 | YES | 2.5
5 | 3.3 | 207 | 683.1 | 22.7 | 7.4 | 24.5476 | YES | 0
6 | 3.5 | 207 | 724.5 | 22.8 | 7.4 | 24.9489 | YES | 2.5
7 | 3.5 | 207 | 724.5 | 22.8 | 7.4 | 24.9489 | YES | 2.5
8 | 3.5 | 207 | 724.5 | 22.9 | 7.4 | 24.782 | YES | 2.5
9 | 3.4 | 207 | 703.8 | 22.7 | 7.3 | 23.9213 | YES | 2.5
10 | 3.1 | 207 | 641.7 | 22.9 | 7.4 | 23.6703 | YES | 0
11 | 3 | 207 | 621 | 23 | 7.4 | 23.2431 | YES | 2.5
12 | 3 | 207 | 621 | 22.9 | 7.4 | 23.4 | YES | 2.5
13 | 3.1 | 207 | 641.7 | 22.8 | 7.4 | 23.83 | YES | 2.5
14 | 3 | 207 | 621 | 23.7 | 7.4 | 22.1729 | YES | 2.5
15 | 1.9 | 207 | 393.3 | 23.5 | 7.4 | 19.7968 | YES | 2.5
16 | 1.3 | 207 | 269.1 | 23.7 | 7.4 | 18.2196 | YES | 2.5
17 | 1.3 | 207 | 269.1 | 23.3 | 7.4 | 18.721 | YES | 2.5
18 | 1.2 | 207 | 248.4 | 23.1 | 7.4 | 18.7582 | YES | 2.5
19 | 1.3 | 207 | 269.1 | 22.9 | 7.4 | 19.2357 | YES | 2.5
20 | 1.1 | 207 | 227.7 | 23.1 | 7.4 | 18.5421 | YES | 0
21 | 1.2 | 207 | 248.4 | 23 | 7.4 | 18.8858 | YES | 2.5
22 | 1.1 | 207 | 227.7 | 22.8 | 7.4 | 18.9233 | YES | 0
23 | 1 | 207 | 207 | 25.5 | 7.4 | 15.5632 | YES | 2.5
24 | 1.2 | 207 | 248.4 | 23.9 | 7.4 | 17.7663 | YES | 2.5
25 | 1 | 207 | 207 | 23.2 | 7.4 | 18.2044 | YES | 2.5
26 | 0.9 | 207 | 186.3 | 23.1 | 7.4 | 18.1171 | YES | 2
27 | 0.7 | 207 | 144.9 | 23.5 | 7.4 | 17.2261 | YES | 0
28 | 0.8 | 207 | 165.6 | 23.2 | 7.4 | 17.7868 | YES | 2
29 | 0.6 | 207 | 124.2 | 22.9 | 7.4 | 17.7366 | YES | 2
30 | 0.7 | 207 | 144.9 | 23 | 7.4 | 17.8222 | YES | 0
31 | 0.5 | 207 | 103.5 | 23.2 | 7.4 | 17.1775 | YES | 0
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2