## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-10-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 44 | 42 | 2 |  | 0.039 | 0.04
2 | 42 | 40 | 2 |  | 0.04 | 0.04
3 | 42 | 40 | 2 |  | 0.04 | 0.04
4 | 0 | 0 | 0 |  | 0.04 | 0.04
5 | 0 | 0 | 0 |  | 0.04 | 0.04
6 | 34 | 32 | 2 |  | 0.04 | 0.04
7 | 38 | 36 | 2 |  | 0.04 | 0.04
8 | 38 | 36 | 2 |  | 0.04 | 0.04
9 | 0 | 0 | 0 |  | 0.04 | 0.04
10 | 36 | 34 | 2 |  | 0.04 | 0.04
11 | 0 | 0 | 0 |  | 0.04 | 0.04
12 | 0 | 0 | 0 |  | 0.04 | 0.04
13 | 0 | 0 | 0 |  | 0.04 | 0.04
14 | 38 | 36 | 2 |  | 0.04 | 0.04
15 | 36 | 34 | 2 |  | 0.04 | 0.04
16 | 0 | 0 | 0 |  | 0.04 | 0.04
17 | 0 | 0 | 0 |  | 0.04 | 0.04
18 | 38 | 36 | 2 |  | 0.04 | 0.04
19 | 38 | 36 | 2 |  | 0.04 | 0.04
20 | 34 | 32 | 2 |  | 0.04 | 0.04
21 | 36 | 34 | 2 |  | 0.04 | 0.04
22 | 38 | 36 | 2 |  | 0.04 | 0.04
23 | 36 | 34 | 2 |  | 0.04 | 0.04
24 | 36 | 34 | 2 |  | 0.04 | 0.04
25 | 42 | 40 | 2 |  | 0.04 | 0.04
26 | 34 | 32 | 2 |  | 0.04 | 0.04
27 | 38 | 36 | 2 |  | 0.04 | 0.04
28 | 36 | 34 | 2 |  | 0.04 | 0.04
29 | 0 | 0 | 0 |  | 0.04 | 0.04
30 | 0 | 0 | 0 |  | 0.04 | 0.04
31 | 0 | 0 | 0 |  | 0.04 | 0.04
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2024-11-05
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2024-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.9 | 207 | 393.3 | 19.3 | 7.4 | 26.2672 | YES | 2.5
2 | 2.2 | 207 | 455.4 | 18.9 | 7.4 | 27.9218 | YES | 2.5
3 | 2.1 | 207 | 434.7 | 18.7 | 7.4 | 27.9765 | YES | 2.5
4 | 0.8 | 207 | 165.6 | 18.5 | 7.4 | 24.4337 | YES | 0
5 | 2 | 207 | 414 | 19 | 7.4 | 27.1088 | YES | 0
6 | 2.1 | 207 | 434.7 | 19.2 | 7.4 | 27.0558 | YES | 2.5
7 | 2 | 207 | 414 | 18.8 | 7.4 | 27.4742 | YES | 2.5
8 | 2.1 | 207 | 434.7 | 18.9 | 7.4 | 27.6046 | YES | 2.5
9 | 1.9 | 207 | 393.3 | 19.1 | 7.4 | 26.6216 | YES | 0
10 | 2.2 | 207 | 455.4 | 18.5 | 7.4 | 28.6788 | YES | 2.5
11 | 2 | 207 | 414 | 18.2 | 7.4 | 28.5993 | YES | 0
12 | 2.2 | 207 | 455.4 | 17.3 | 7.4 | 31.0716 | YES | 0
13 | 2.1 | 207 | 434.7 | 17.9 | 7.4 | 29.5133 | YES | 0
14 | 2 | 207 | 414 | 18 | 7.4 | 28.9842 | YES | 2.5
15 | 2.1 | 207 | 434.7 | 17.2 | 7.4 | 30.9252 | YES | 2.5
16 | 2.1 | 207 | 434.7 | 16.8 | 7.4 | 31.7613 | YES | 0
17 | 2 | 207 | 414 | 16.5 | 7.4 | 32.0361 | YES | 0
18 | 2.1 | 207 | 434.7 | 16.2 | 7.4 | 33.0569 | YES | 2.5
19 | 2 | 207 | 414 | 16.4 | 7.4 | 32.2503 | YES | 2.5
20 | 2 | 207 | 414 | 16.8 | 7.4 | 31.4017 | YES | 2.5
21 | 2.1 | 207 | 434.7 | 16.5 | 7.4 | 32.4028 | YES | 2.5
22 | 1.9 | 207 | 393.3 | 15.7 | 7.4 | 33.4076 | YES | 2.5
23 | 2 | 207 | 414 | 15 | 7.4 | 35.4006 | YES | 2.5
24 | 2 | 207 | 414 | 14.6 | 7.5 | 37.7209 | YES | 2.5
25 | 2.1 | 207 | 434.7 | 14.9 | 7.5 | 37.3986 | YES | 2.5
26 | 1.9 | 207 | 393.3 | 15 | 7.4 | 35.0008 | YES | 2.5
27 | 1.5 | 207 | 310.5 | 14.6 | 7.5 | 35.6404 | YES | 2.5
28 | 1.6 | 207 | 331.2 | 14.8 | 7.5 | 35.5712 | YES | 2.5
29 | 1.7 | 207 | 351.9 | 14.4 | 7.5 | 36.9465 | YES | 0
30 | 1.9 | 207 | 393.3 | 14.6 | 7.5 | 37.2955 | YES | 0
31 | 1.6 | 207 | 331.2 | 12.5 | 7.5 | 41.4388 | YES | 0
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2