## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-02-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 |  | 0.016 | 0.02
2 | 0 | 0 | 0 |  | 0.02 | 0.02
3 | 0 | 0 | 0 |  | 0.02 | 0.02
4 | 0 | 0 | 0 |  | 0.02 | 0.02
5 | 0 | 0 | 0 |  | 0.02 | 0.02
6 | 44 | 42 | 2 |  | 0.02 | 0.02
7 | 44 | 42 | 2 |  | 0.02 | 0.02
8 | 44 | 42 | 2 |  | 0.02 | 0.02
9 | 44 | 42 | 2 |  | 0.02 | 0.02
10 | 0 | 0 | 0 |  | 0.02 | 0.02
11 | 0 | 0 | 0 |  | 0.02 | 0.02
12 | 44 | 42 | 2 |  | 0.02 | 0.02
13 | 0 | 0 | 0 |  | 0.02 | 0.02
14 | 44 | 42 | 2 |  | 0.02 | 0.02
15 | 44 | 42 | 2 |  | 0.02 | 0.02
16 | 0 | 0 | 0 |  | 0.02 | 0.02
17 | 44 | 42 | 2 |  | 0.02 | 0.02
18 | 44 | 42 | 2 |  | 0.02 | 0.02
19 | 0 | 0 | 0 |  | 0.02 | 0.02
20 | 44 | 42 | 2 |  | 0.02 | 0.02
21 | 44 | 42 | 2 |  | 0.02 | 0.02
22 | 0 | 0 | 0 |  | 0.02 | 0.02
23 | 0 | 0 | 0 |  | 0.02 | 0.02
24 | 44 | 42 | 2 |  | 0.02 | 0.02
25 | 44 | 42 | 2 |  | 0.02 | 0.02
26 | 0 | 0 | 0 |  | 0.02 | 0.02
27 | 44 | 42 | 2 |  | 0.02 | 0.02
28 | 0 | 0 | 0 |  | 0.02 | 0.02
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2025-03-02
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2025-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 207 | 165.6 | 5.9 | 7 | 49.4343 | YES | 0
2 | 0.9 | 207 | 186.3 | 5 | 7 | 53.1105 | YES | 0
3 | 0.9 | 207 | 186.3 | 2.9 | 6.8 | 56.9432 | YES | 0
4 | 1 | 207 | 207 | 3.2 | 6.8 | 56.4501 | YES | 0
5 | 1.2 | 207 | 248.4 | 4.7 | 6.9 | 54.1227 | YES | 0
6 | 1.4 | 207 | 289.8 | 5.8 | 7 | 53.3113 | YES | 3
7 | 1.3 | 207 | 269.1 | 5.5 | 7.1 | 55.7397 | YES | 3
8 | 1.2 | 207 | 248.4 | 5.6 | 7.1 | 54.73 | YES | 3
9 | 1.4 | 207 | 289.8 | 5.8 | 7.1 | 55.2579 | YES | 3
10 | 1.1 | 207 | 227.7 | 4.3 | 7.1 | 59.0668 | YES | 0
11 | 1 | 207 | 207 | 4.1 | 6.9 | 55.0694 | YES | 0
12 | 1.3 | 207 | 269.1 | 4.7 | 6.8 | 52.823 | YES | 3
13 | 1.4 | 207 | 289.8 | 5.6 | 6.9 | 52.1332 | YES | 0
14 | 1.5 | 207 | 310.5 | 5.7 | 7.1 | 56.2781 | YES | 3
15 | 1.4 | 207 | 289.8 | 5.9 | 7.2 | 56.8958 | YES | 3
16 | 1.4 | 207 | 289.8 | 5.8 | 7.2 | 57.2816 | YES | 3
17 | 1.5 | 207 | 310.5 | 6.1 | 7.3 | 58.8697 | YES | 3
18 | 1.6 | 207 | 331.2 | 6.3 | 7.3 | 58.7551 | YES | 3
19 | 2.7 | 207 | 558.9 | 6.7 | 7.3 | 64.9909 | YES | 0
20 | 3.2 | 207 | 662.4 | 6.6 | 7.3 | 69.3829 | YES | 3
21 | 3 | 207 | 621 | 7.3 | 7.2 | 62.306 | YES | 3
22 | 2.2 | 207 | 455.4 | 6.7 | 7.2 | 59.1326 | YES | 0
23 | 2 | 207 | 414 | 6.1 | 7.2 | 60.1744 | YES | 0
24 | 1.6 | 207 | 331.2 | 6.9 | 7.3 | 56.4188 | YES | 3
25 | 1.7 | 207 | 351.9 | 7.1 | 7.3 | 56.3094 | YES | 3
26 | 1.6 | 207 | 331.2 | 6.8 | 7.3 | 56.8011 | YES | 0
27 | 1.4 | 207 | 289.8 | 7.4 | 7.3 | 53.3064 | YES | 3
28 | 1.5 | 207 | 310.5 | 7.9 | 7.3 | 52.1428 | YES | 0
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2