## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-02
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 |  | 0.02 | 0.02
2 | 0 | 0 | 0 |  | 0.02 | 0.02
3 | 44 | 42 | 2 |  | 0.02 | 0.02
4 | 0 | 0 | 0 |  | 0.02 | 0.02
5 | 44 | 42 | 2 |  | 0.02 | 0.02
6 | 0 | 0 | 0 |  | 0.02 | 0.02
7 | 0 | 0 | 0 |  | 0.02 | 0.02
8 | 0 | 0 | 0 |  | 0.02 | 0.02
9 | 44 | 42 | 2 |  | 0.02 | 0.02
10 | 0 | 0 | 0 |  | 0.02 | 0.02
11 | 44 | 42 | 2 |  | 0.02 | 0.02
12 | 0 | 0 | 0 |  | 0.02 | 0.02
13 | 0 | 0 | 0 |  | 0.02 | 0.02
14 | 44 | 42 | 2 |  | 0.02 | 0.02
15 | 0 | 0 | 0 |  | 0.02 | 0.02
16 | 0 | 0 | 0 |  | 0.02 | 0.02
17 | 0 | 0 | 0 |  | 0.02 | 0.02
18 | 44 | 42 | 2 |  | 0.02 | 0.02
19 | 44 | 42 | 2 |  | 0.02 | 0.02
20 | 44 | 42 | 2 |  | 0.02 | 0.02
21 | 0 | 0 | 0 |  | 0.02 | 0.02
22 | 0 | 0 | 0 |  | 0.02 | 0.02
23 | 0 | 0 | 0 |  | 0.02 | 0.02
24 | 44 | 42 | 2 |  | 0.02 | 0.02
25 | 44 | 42 | 2 |  | 0.02 | 0.02
26 | 44 | 42 | 2 |  | 0.02 | 0.02
27 | 44 | 0 | 44 |  | 0.02 | 0.02
28 | 0 | 0 | 0 |  | 0.02 | 0.02
29 | 0 | 0 | 0 |  | 0.02 | 0.02
30 | 0 | 0 | 0 |  | 0.02 | 0.02
31 | 44 | 42 | 2 |  | 0.02 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 4/2/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2025-04-02 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.4 | 207 | 289.8 | 6.9 | 7.3 | 55.1305 | YES | 0
2 | 1.5 | 207 | 310.5 | 7.2 | 7.4 | 56.6542 | YES | 0
3 | 1.5 | 2025-02-07 | 68542.5 | 8 | 7.4 | 53.6807 | YES | 3
4 | 1.5 | 207 | 310.5 | 8.6 | 7.5 | 53.4391 | YES | 0
5 | 1.5 | 207 | 310.5 | 8.8 | 7.4 | 50.876 | YES | 3
6 | 1.4 | 207 | 289.8 | 7.8 | 7.4 | 53.7847 | YES | 0
7 | 1.4 | 207 | 289.8 | 6.1 | 7.3 | 58.1911 | YES | 0
8 | 1.5 | 207 | 310.5 | 7.9 | 7.4 | 54.043 | YES | 0
9 | 1.6 | 207 | 331.2 | 9.7 | 7.2 | 45.1497 | YES | 3
10 | 1.5 | 207 | 310.5 | 8.1 | 7.3 | 51.4485 | YES | 0
11 | 1.6 | 207 | 331.2 | 8.2 | 7.2 | 49.884 | YES | 3
12 | 1.5 | 207 | 310.5 | 7.4 | 7.2 | 52.0279 | YES | 0
13 | 1.6 | 207 | 331.2 | 8.1 | 7.3 | 52.0423 | YES | 3
14 | 1.6 | 207 | 331.2 | 7.6 | 7.3 | 53.8194 | YES | 0
15 | 1.5 | 207 | 310.5 | 7 | 7.3 | 55.3958 | YES | 0
16 | 1.4 | 207 | 289.8 | 6.8 | 7.2 | 53.5474 | YES | 3
17 | 1.5 | 207 | 310.5 | 7.6 | 7.2 | 51.3353 | YES | 0
18 | 1.7 | 207 | 351.9 | 8.3 | 7.3 | 51.942 | YES | 0
19 | 1.6 | 207 | 331.2 | 7.4 | 7.3 | 54.5486 | YES | 0
20 | 1.7 | 207 | 351.9 | 8 | 7.4 | 54.9324 | YES | 3
21 | 1.5 | 207 | 310.5 | 7.4 | 7.3 | 53.9236 | YES | 3
22 | 1.6 | 207 | 331.2 | 8.8 | 7.4 | 51.4626 | YES | 3
23 | 1.9 | 207 | 393.3 | 9.5 | 7.4 | 50.8247 | YES | 0
24 | 2 | 207 | 414 | 10 | 7.2 | 46.3156 | YES | 3
25 | 2.1 | 207 | 434.7 | 9.8 | 7.2 | 47.4715 | YES | 3
26 | 2 | 207 | 414 | 13.9 | 7 | 32.8543 | YES | 3
27 | 1.9 | 207 | 393.3 | 12.4 | 7.1 | 37.784 | YES | 3
28 | 1.7 | 207 | 351.9 | 8.9 | 7.2 | 48.1556 | YES | 0
29 | 1.6 | 207 | 331.2 | 8.1 | 7.2 | 50.2184 | YES | 0
30 | 1.5 | 207 | 310.5 | 7.8 | 7.3 | 52.4938 | YES | 0
31 | 1.7 | 207 | 351.9 | 8.9 | 7.2 | 48.1556 | YES | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2