## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 |  | 0.02 | 0.2
2 | 44 | 42 | 2 |  | 0.02 | 0.02
3 | 0 | 0 | 0 |  | 0.02 | 0.2
4 | 0 | 0 | 0 |  | 0.02 | 0.02
5 | 44 | 42 | 2 |  | 0.02 | 0.02
6 | 0 | 0 | 0 |  | 0.02 | 0.02
7 | 44 | 42 | 2 |  | 0.02 | 0.02
8 | 0 | 0 | 0 |  | 0.02 | 0.02
9 | 0 | 0 | 0 |  | 0.02 | 0.02
10 | 0 | 0 | 0 |  | 0.02 | 0.02
11 | 44 | 42 | 2 |  | 0.02 | 0.02
12 | 0 | 0 | 0 |  | 0.02 | 0.02
13 | 44 | 42 | 2 |  | 0.02 | 0.02
14 | 0 | 0 | 0 |  | 0.02 | 0.02
15 | 0 | 0 | 0 |  | 0.02 | 0.02
16 | 0 | 0 | 0 |  | 0.02 | 0.02
17 | 0 | 0 | 0 |  | 0.02 | 0.02
18 | 0 | 0 | 0 |  | 0.02 | 0.02
19 | 44 | 42 | 2 |  | 0.02 | 0.02
20 | 0 | 0 | 0 |  | 0.02 | 0.02
21 | 44 | 42 | 2 |  | 0.02 | 0.02
22 | 44 | 42 | 2 |  | 0.014 | 0.01
23 | 44 | 42 | 2 |  | 0.02 | 0.02
24 | 44 | 42 | 2 |  | 0.02 | 0.02
25 | 44 | 42 | 2 |  | 0.02 | 0.02
26 | 44 | 42 | 2 |  | 0.02 | 0.02
27 | 44 | 42 | 2 |  | 0.02 | 0.02
28 | 44 | 42 | 2 |  | 0.02 | 0.02
29 | 44 | 42 | 2 |  | 0.02 | 0.02
30 | 0 | 0 | 0 |  | 0.014 | 0.01
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: May 5, 2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287 - 2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 207 | 310.5 | 7.1 | 7.3 | 55.0237 | YES | 0
2 | 1.8 | 207 | 372.6 | 9.3 | 7.1 | 45.7804 | YES | 3
3 | 1.9 | 207 | 393.3 | 9.5 | 7.2 | 47.3377 | YES | 0
4 | 1.8 | 207 | 372.6 | 9.3 | 7.2 | 47.4283 | YES | 0
5 | 1.9 | 207 | 393.3 | 10.7 | 7.3 | 45.289 | YES | 3
6 | 1.9 | 207 | 393.3 | 9.9 | 7.2 | 46.0974 | YES | 0
7 | 1.8 | 207 | 372.6 | 10.2 | 7.3 | 46.2862 | YES | 3
8 | 1.7 | 207 | 351.9 | 9.4 | 7.2 | 46.5815 | YES | 0
9 | 1.8 | 207 | 372.6 | 9.7 | 7.3 | 47.8493 | YES | 0
10 | 1.7 | 207 | 351.9 | 10.5 | 7.3 | 44.8643 | YES | 0
11 | 1.9 | 207 | 393.3 | 11.6 | 7.3 | 42.6787 | YES | 3
12 | 1.7 | 207 | 351.9 | 9.9 | 7.2 | 45.0639 | YES | 0
13 | 1.8 | 207 | 372.6 | 10.9 | 7.3 | 44.1915 | YES | 3
14 | 1.6 | 207 | 331.2 | 9.6 | 7.2 | 45.4494 | YES | 0
15 | 1.6 | 207 | 331.2 | 10.1 | 7.3 | 45.5485 | YES | 0
16 | 1.7 | 207 | 351.9 | 10.7 | 7.3 | 44.2755 | YES | 0
17 | 1.6 | 207 | 331.2 | 10.4 | 7.3 | 44.6536 | YES | 0
18 | 1.7 | 207 | 351.9 | 10.5 | 7.3 | 44.8643 | YES | 0
19 | 1.8 | 207 | 372.6 | 10.1 | 7.5 | 50.0211 | YES | 3
20 | 1.6 | 207 | 331.2 | 9.6 | 7.2 | 45.4494 | YES | 0
21 | 1.5 | 207 | 310.5 | 10.9 | 7.3 | 42.721 | YES | 0
22 | 1.6 | 207 | 331.2 | 11.1 | 7.3 | 42.6402 | YES | 3
23 | 1.7 | 207 | 351.9 | 10.8 | 7.3 | 43.9843 | YES | 3
24 | 1.5 | 207 | 310.5 | 11.2 | 7.3 | 41.8874 | YES | 3
25 | 1.6 | 207 | 331.2 | 10.8 | 7.3 | 43.4905 | YES | 3
26 | 1.5 | 207 | 310.5 | 7.7 | 7.2 | 50.9927 | YES | 3
27 | 1.6 | 207 | 331.2 | 9.8 | 7.3 | 46.4631 | YES | 3
28 | 1.5 | 207 | 310.5 | 10.8 | 7.3 | 43.0029 | YES | 3
29 | 1.6 | 207 | 331.2 | 10.6 | 7.3 | 44.0678 | YES | 0
30 | 1.5 | 207 | 310.5 | 9.4 | 7.3 | 47.1742 | YES | 0
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2