## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 44 | 42 | 2 |  | 0.015 | 0.02
2 | 44 | 42 | 2 |  | 0.02 | 0.02
3 | 0 | 0 | 0 |  | 0.01 | 0.01
4 | 44 | 42 | 2 |  | 0.02 | 0.02
5 | 44 | 42 | 2 |  | 0.01 | 0.01
6 | 44 | 42 | 2 |  | 0.02 | 0.02
7 | 44 | 42 | 2 |  | 0.01 | 0.01
8 | 0 | 0 | 0 |  | 0.01 | 0.01
9 | 44 | 42 | 2 |  | 0.01 | 0.01
10 | 44 | 42 | 2 |  | 0.01 | 0.01
11 | 44 | 42 | 2 |  | 0.01 | 0.01
12 | 44 | 42 | 2 |  | 0.02 | 0.02
13 | 44 | 42 | 2 |  | 0.02 | 0.02
14 | 44 | 42 | 2 |  | 0.02 | 0.02
15 | 44 | 42 | 2 |  | 0.01 | 0.01
16 | 44 | 42 | 2 |  | 0.01 | 0.01
17 | 44 | 42 | 2 |  | 0.02 | 0.02
18 | 44 | 42 | 2 |  | 0.02 | 0.02
19 | 44 | 42 | 2 |  | 0.02 | 0.02
20 | 0 | 0 | 0 |  | 0.01 | 0.01
21 | 44 | 42 | 2 |  | 0.01 | 0.01
22 | 44 | 42 | 2 |  | 0.02 | 0.02
23 | 44 | 42 | 2 |  | 0.02 | 0.02
24 | 44 | 42 | 2 |  | 0.02 | 0.02
25 | 44 | 42 | 2 |  | 0.01 | 0.01
26 | 44 | 42 | 2 |  | 0.01 | 0.01
27 | 44 | 42 | 2 |  | 0.01 | 0.01
28 | 44 | 42 | 2 |  | 0.01 | 0.01
29 | 44 | 42 | 2 |  | 0.01 | 0.01
30 | 44 | 42 | 2 |  | 0.01 | 0.01
31 | 44 | 42 | 2 |  | 0.01 | 0.01
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 6/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287-2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.6 | 207 | 331.2 | 13.2 | 7.1 | 34.1304 | YES | 3
2 | 1.5 | 207 | 310.5 | 14.6 | 7.1 | 30.7385 | YES | 3
3 | 1.4 | 207 | 289.8 | 12.4 | 7.1 | 35.7515 | YES | 0
4 | 1.5 | 207 | 310.5 | 13.4 | 7.1 | 33.2983 | YES | 3
5 | 1.6 | 207 | 331.2 | 12.1 | 7.2 | 38.5748 | YES | 3
6 | 1.1 | 207 | 227.7 | 14.2 | 7.2 | 31.302 | YES | 3
7 | 1.3 | 207 | 269.1 | 13.7 | 7.2 | 33.1078 | YES | 3
8 | 1 | 207 | 207 | 13.1 | 7.1 | 32.092 | YES | 0
9 | 1.1 | 207 | 227.7 | 15.9 | 7.2 | 27.942 | YES | 3
10 | 0.9 | 207 | 186.3 | 16.3 | 7.3 | 27.5961 | YES | 3
11 | 0.9 | 207 | 186.3 | 15.4 | 7.2 | 28.2397 | YES | 3
12 | 1 | 207 | 207 | 14.5 | 7.3 | 31.4791 | YES | 3
13 | 0.9 | 207 | 186.3 | 13.9 | 7.3 | 32.3928 | YES | 3
14 | 0.8 | 207 | 165.6 | 13.1 | 7.2 | 32.5526 | YES | 3
15 | 0.6 | 207 | 124.2 | 13.8 | 7.3 | 31.5147 | YES | 3
16 | 0.7 | 207 | 144.9 | 15.2 | 7.3 | 29.0319 | YES | 3
17 | 0.8 | 207 | 165.6 | 14.6 | 7.3 | 30.5654 | YES | 3
18 | 0.6 | 207 | 124.2 | 13.6 | 7.3 | 31.9377 | YES | 3
19 | 0.6 | 207 | 124.2 | 14.1 | 7.3 | 30.8903 | YES | 3
20 | 0.5 | 207 | 103.5 | 16.8 | 7.3 | 25.4931 | YES | 0
21 | 0.5 | 207 | 103.5 | 17.1 | 7.3 | 24.985 | YES | 3
22 | 0.6 | 207 | 124.2 | 16.8 | 7.3 | 25.7867 | YES | 3
23 | 0.7 | 207 | 144.9 | 16.9 | 7.4 | 26.8918 | YES | 3
24 | 0.8 | 207 | 165.6 | 17.6 | 7.4 | 25.9549 | YES | 3
25 | 0.7 | 207 | 144.9 | 17.1 | 7.4 | 26.5339 | YES | 3
26 | 0.8 | 207 | 165.6 | 18.3 | 7.3 | 23.8571 | YES | 3
27 | 0.9 | 207 | 186.3 | 18.6 | 7.3 | 23.6507 | YES | 3
28 | 0.8 | 207 | 165.6 | 18.4 | 7.3 | 23.6972 | YES | 3
29 | 0.9 | 207 | 186.3 | 19.9 | 7.4 | 22.4947 | YES | 3
30 | 0.7 | 207 | 144.9 | 22.6 | 7.4 | 18.3131 | YES | 3
31 | 0.6 | 207 | 124.2 | 21.4 | 7.4 | 19.6366 | YES | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2