## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-09-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 |  | 0.01 | 0.01
2 | 44 | 42 | 2 |  | 0.01 | 0.01
3 | 0 | 0 | 0 |  | 0.01 | 0.01
4 | 44 | 42 | 2 |  | 0.01 | 0.01
5 | 44 | 42 | 2 |  | 0.01 | 0.01
6 | 44 | 42 | 2 |  | 0.01 | 0.01
7 | 44 | 42 | 2 |  | 0.01 | 0.01
8 | 44 | 42 | 2 |  | 0.01 | 0.01
9 | 44 | 42 | 2 |  | 0.01 | 0.01
10 | 0 | 0 | 0 |  | 0.01 | 0.01
11 | 0 | 0 | 0 |  | 0.01 | 0.01
12 | 0 | 0 | 0 |  | 0.01 | 0.01
13 | 0 | 0 | 0 |  | 0.01 | 0.01
14 | 44 | 42 | 2 |  | 0.01 | 0.01
15 | 44 | 42 | 2 |  | 0.01 | 0.01
16 | 0 | 0 | 0 |  | 0.01 | 0.01
17 | 44 | 42 | 2 |  | 0.01 | 0.01
18 | 0 | 0 | 0 |  | 0.01 | 0.01
19 | 44 | 42 | 2 |  | 0.01 | 0.01
20 | 0 | 0 | 0 |  | 0.01 | 0.01
21 | 44 | 42 | 2 |  | 0.01 | 0.01
22 | 44 | 42 | 2 |  | 0.01 | 0.01
23 | 44 | 42 | 2 |  | 0.01 | 0.01
24 | 0 | 0 | 0 |  | 0.01 | 0.01
25 | 44 | 42 | 2 |  | 0.01 | 0.01
26 | 0 | 0 | 0 |  | 0.01 | 0.01
27 | 0 | 0 | 0 |  | 0.01 | 0.01
28 | 44 | 42 | 2 |  | 0.01 | 0.01
29 | 44 | 42 | 2 |  | 0.01 | 0.01
30 | 0 | 0 | 0 |  | 0.01 | 0.01
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 10/5/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287-2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 207 | 207 | 23.9 | 7.5 | 18.0264 | YES | 0
2 | 1 | 207 | 207 | 23.6 | 7.5 | 18.3975 | YES | 3
3 | 0.9 | 207 | 186.3 | 22.8 | 7.5 | 19.1996 | YES | 0
4 | 1 | 207 | 207 | 23.4 | 7.5 | 18.6489 | YES | 3
5 | 1 | 207 | 207 | 23.5 | 7.5 | 18.5228 | YES | 3
6 | 0.9 | 207 | 186.3 | 23.1 | 7.5 | 18.8131 | YES | 3
7 | 1 | 207 | 207 | 22.9 | 7.5 | 19.2919 | YES | 3
8 | 1 | 207 | 207 | 22.6 | 7.5 | 19.6878 | YES | 3
9 | 1 | 207 | 207 | 22 | 7.5 | 20.5033 | YES | 3
10 | 1.1 | 207 | 227.7 | 22.6 | 7.5 | 19.9167 | YES | 0
11 | 1 | 207 | 207 | 21.4 | 7.5 | 21.3512 | YES | 0
12 | 1.3 | 207 | 269.1 | 21.7 | 7.5 | 21.6592 | YES | 0
13 | 1.5 | 207 | 310.5 | 21.6 | 7.5 | 22.3136 | YES | 0
14 | 1.6 | 207 | 331.2 | 20.9 | 7.5 | 23.6605 | YES | 3
15 | 1.4 | 207 | 289.8 | 20.2 | 7.5 | 24.2375 | YES | 3
16 | 1 | 207 | 207 | 21 | 7.5 | 21.9351 | YES | 0
17 | 1.3 | 207 | 269.1 | 21.5 | 7.5 | 21.9533 | YES | 3
18 | 1.2 | 207 | 248.4 | 20.7 | 7.5 | 22.9039 | YES | 0
19 | 1.2 | 207 | 248.4 | 20.4 | 7.5 | 23.371 | YES | 3
20 | 1.4 | 207 | 289.8 | 20 | 7.5 | 24.5653 | YES | 0
21 | 1.2 | 207 | 248.4 | 20.2 | 7.5 | 23.6874 | YES | 3
22 | 1.2 | 207 | 248.4 | 19.9 | 7.5 | 24.17 | YES | 3
23 | 1.3 | 207 | 269.1 | 19.7 | 7.5 | 24.7794 | YES | 3
24 | 1.2 | 207 | 248.4 | 20 | 7.5 | 24.0081 | YES | 0
25 | 1.1 | 207 | 227.7 | 19.8 | 7.5 | 24.0553 | YES | 3
26 | 1.2 | 207 | 248.4 | 19.4 | 7.5 | 24.9953 | YES | 0
27 | 1.2 | 207 | 248.4 | 19.1 | 7.5 | 25.5036 | YES | 0
28 | 1.1 | 207 | 227.7 | 18.7 | 7.5 | 25.8987 | YES | 3
29 | 1.2 | 207 | 248.4 | 19.2 | 7.5 | 25.3331 | YES | 3
30 | 1.3 | 207 | 269.1 | 19.5 | 7.5 | 25.1144 | YES | 0
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2