## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-01-01
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 44 | 42 | 2 |  | 0.01 | 0.01
2 | 44 | 42 | 2 |  | 0.01 | 0.01
3 | 44 | 42 | 2 |  | 0.01 | 0.01
4 | 44 | 42 | 2 |  | 0.01 | 0.01
5 | 44 | 42 | 2 |  | 0.01 | 0.01
6 | 44 | 42 | 2 |  | 0.01 | 0.01
7 | 44 | 42 | 2 |  | 0.01 | 0.01
8 | 44 | 42 | 2 |  | 0.01 | 0.01
9 | 44 | 42 | 2 |  | 0.01 | 0.01
10 | 44 | 42 | 2 |  | 0.01 | 0.01
11 | 44 | 42 | 2 |  | 0.01 | 0.01
12 | 44 | 42 | 2 |  | 0.01 | 0.01
13 | 44 | 42 | 2 |  | 0.01 | 0.01
14 | 44 | 42 | 2 |  | 0.01 | 0.01
15 | 44 | 42 | 2 |  | 0.01 | 0.01
16 | 45 | 43 | 2 |  | 0.02 | 0.02
17 | 45 | 43 | 2 |  | 0.02 | 0.02
18 | 45 | 43 | 2 |  | 0.02 | 0.02
19 | 45 | 43 | 2 |  | 0.02 | 0.02
20 | 45 | 43 | 2 |  | 0.02 | 0.02
21 | 45 | 43 | 2 |  | 0.01 | 0.01
22 | 45 | 43 | 2 |  | 0.02 | 0.02
23 | 45 | 43 | 2 |  | 0.02 | 0.02
24 | 45 | 43 | 2 |  | 0.01 | 0.01
25 | 45 | 43 | 2 |  | 0.02 | 0.02
26 | 45 | 43 | 2 |  | 0.01 | 0.01
27 | 45 | 43 | 2 |  | 0.02 | 0.02
28 | 45 | 43 | 2 |  | 0.02 | 0.02
29 | 45 | 43 | 2 |  | 0.02 | 0.02
30 | 45 | 43 | 2 |  | 0.02 | 0.02
31 | 45 | 43 | 2 |  | 0.02 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:2/2/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287-2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 207 | 186.3 | 9.3 | 7.5 | 47.6101 | YES | 3
2 | 3.5 | 207 | 724.5 | 9.8 | 7.4 | 59.9065 | YES | 3
3 | 3.5 | 207 | 724.5 | 9.3 | 7.4 | 61.976 | YES | 3
4 | 3.5 | 207 | 724.5 | 9.5 | 7.4 | 61.1391 | YES | 3
5 | 3.5 | 207 | 724.5 | 9.4 | 7.3 | 59.3692 | YES | 3
6 | 3.5 | 207 | 724.5 | 8.9 | 7.3 | 61.4186 | YES | 3
7 | 3.5 | 207 | 724.5 | 8.2 | 7.3 | 64.4165 | YES | 3
8 | 3.3 | 207 | 683.1 | 7.5 | 7.2 | 63.6511 | YES | 3
9 | 2.5 | 207 | 517.5 | 7 | 7.2 | 59.9957 | YES | 3
10 | 3 | 207 | 621 | 7.4 | 7.2 | 61.8837 | YES | 3
11 | 3.2 | 207 | 662.4 | 7.5 | 7.2 | 62.9131 | YES | 3
12 | 3.1 | 207 | 641.7 | 7.7 | 7.2 | 61.3443 | YES | 3
13 | 2.9 | 207 | 600.3 | 8.4 | 7.2 | 57.1598 | YES | 3
14 | 2.7 | 207 | 558.9 | 8.1 | 7.2 | 56.996 | YES | 3
15 | 3 | 207 | 621 | 8.3 | 7.2 | 58.2181 | YES | 3
16 | 1 | 207 | 207 | 8.9 | 7.2 | 44.4762 | YES | 3
17 | 1.1 | 207 | 227.7 | 8.6 | 7.2 | 45.8844 | YES | 3
18 | 1 | 207 | 207 | 8.2 | 7.2 | 46.5858 | YES | 3
19 | 0.9 | 207 | 186.3 | 8.8 | 7.3 | 45.8553 | YES | 3
20 | 1 | 207 | 207 | 8.9 | 7.3 | 46.0723 | YES | 3
21 | 1 | 207 | 207 | 9.2 | 7.3 | 45.1661 | YES | 3
22 | 1 | 207 | 207 | 8.6 | 7.3 | 46.9985 | YES | 3
23 | 0.9 | 207 | 186.3 | 8.4 | 7.3 | 47.0884 | YES | 3
24 | 1 | 207 | 207 | 7.9 | 7.3 | 49.2404 | YES | 3
25 | 1.2 | 207 | 248.4 | 7.7 | 7.3 | 51.0582 | YES | 3
26 | 1.1 | 207 | 227.7 | 8.1 | 7.3 | 49.146 | YES | 3
27 | 1 | 207 | 207 | 8.3 | 7.4 | 49.679 | YES | 3
28 | 1.1 | 207 | 227.7 | 8.5 | 7.4 | 49.5837 | YES | 3
29 | 1 | 207 | 207 | 9 | 7.4 | 47.4153 | YES | 3
30 | 1 | 207 | 207 | 9.1 | 7.4 | 47.1013 | YES | 3
31 | 1.1 | 207 | 227.7 | 9.3 | 7.3 | 45.3794 | YES | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2