## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-28
System Name: | Cascade Gorge Properties |  |  | ID#: 41 | 91556 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 45 | 43 | 2 |  | 0.02 | 0.02
2 | 45 | 43 | 2 |  | 0.02 | 0.02
3 | 45 | 43 | 2 |  | 0.02 | 0.02
4 | 45 | 43 | 2 |  | 0.02 | 0.02
5 | 45 | 43 | 2 |  | 0.02 | 0.02
6 | 45 | 43 | 2 |  | 0.02 | 0.02
7 | 45 | 43 | 2 |  | 0.02 | 0.02
8 | 45 | 43 | 2 |  | 0.02 | 0.02
9 | 45 | 43 | 2 |  | 0.02 | 0.02
10 | 45 | 43 | 2 |  | 0.02 | 0.02
11 | 45 | 43 | 2 |  | 0.02 | 0.02
12 | 45 | 43 | 2 |  | 0.01 | 0.01
13 | 45 | 43 | 2 |  | 0.01 | 0.01
14 | 45 | 43 | 2 |  | 0.02 | 0.02
15 | 45 | 43 | 2 |  | 0.01 | 0.01
16 | 45 | 43 | 2 |  | 0.02 | 0.02
17 | 45 | 43 | 2 |  | 0.02 | 0.02
18 | 45 | 43 | 2 |  | 0.02 | 0.02
19 | 45 | 43 | 2 |  | 0.02 | 0.02
20 | 45 | 43 | 2 |  | 0.02 | 0.02
21 | 45 | 43 | 2 |  | 0.01 | 0.01
22 | 45 | 43 | 2 |  | 0.02 | 0.02
23 | 45 | 43 | 2 |  | 0.02 | 0.02
24 | 45 | 43 | 2 |  | 0.02 | 0.02
25 | 45 | 43 | 2 |  | 0.02 | 0.02
26 | 45 | 43 | 2 |  | 0.02 | 0.02
27 | 45 | 43 | 2 |  | 0.02 | 0.02
28 | 45 | 43 | 2 |  | 0.02 | 0.02
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Salena Su
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:3/1/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 287-2197 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2026-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 207 | 248.4 | 9 | 7.4 | 48.5084 | YES | 3
2 | 1 | 207 | 207 | 9.2 | 7.4 | 46.7895 | YES | 3
3 | 0.8 | 207 | 165.6 | 9 | 7.4 | 46.3493 | YES | 3
4 | 0.7 | 207 | 144.9 | 9.6 | 7.4 | 44.0439 | YES | 3
5 | 0.8 | 207 | 165.6 | 10.1 | 7.4 | 43.1 | YES | 3
6 | 0.9 | 207 | 186.3 | 9.9 | 7.4 | 44.1675 | YES | 3
7 | 1.1 | 207 | 227.7 | 9.3 | 7.4 | 47.0114 | YES | 3
8 | 1 | 207 | 207 | 8.8 | 7.4 | 48.0503 | YES | 3
9 | 1.1 | 207 | 227.7 | 9 | 7.4 | 47.9584 | YES | 3
10 | 0.9 | 207 | 186.3 | 8.9 | 7.4 | 47.1914 | YES | 3
11 | 1 | 207 | 207 | 8.7 | 7.4 | 48.3713 | YES | 3
12 | 0.9 | 207 | 186.3 | 9.1 | 7.4 | 46.5688 | YES | 3
13 | 1 | 207 | 207 | 8.8 | 7.4 | 48.0503 | YES | 3
14 | 0.9 | 207 | 186.3 | 8.5 | 7.4 | 48.4641 | YES | 3
15 | 0.8 | 207 | 165.6 | 8.7 | 7.4 | 47.2817 | YES | 3
16 | 0.9 | 207 | 186.3 | 8.4 | 7.4 | 48.7881 | YES | 3
17 | 0.9 | 207 | 186.3 | 7.8 | 7.4 | 50.7828 | YES | 3
18 | 0.8 | 207 | 165.6 | 7.7 | 7.4 | 50.5414 | YES | 3
19 | 1 | 207 | 207 | 7.9 | 7.4 | 51.0255 | YES | 3
20 | 0.8 | 207 | 165.6 | 8.9 | 7.4 | 46.6578 | YES | 3
21 | 0.9 | 207 | 186.3 | 9.2 | 7.4 | 46.2609 | YES | 3
22 | 1 | 207 | 207 | 8.6 | 7.4 | 48.6947 | YES | 3
23 | 0.8 | 207 | 165.6 | 8.4 | 7.4 | 48.2347 | YES | 3
24 | 0.6 | 207 | 124.2 | 7.9 | 7.4 | 48.7436 | YES | 3
25 | 0.4 | 207 | 82.8 | 7.7 | 7.4 | 48.2832 | YES | 3
26 | 0.4 | 207 | 82.8 | 8.1 | 7.4 | 47.0156 | YES | 3
27 | 0.3 | 207 | 62.1 | 8.3 | 7.4 | 45.8719 | YES | 3
28
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2