## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-07-01
System Name: | White Branch Youth Camp |  |  | ID#: 41 | 91783 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 30 | 0
2 | 30 | 30 | 0
3 | no campers |  | #VALUE!
4 | 30 | 30 | 0
5 | 30 | 31 | -1 | 25
6 | 30 | 30 | 0 | 25 | 0.32 | 0.33
7 | 30 | 30 | 0 | 25
8 | 12 | 15 | -3 | 25
9 | 10 | 12 | -2 | 25
10 | no campers |  | #VALUE!
11 | no campers |  | #VALUE!
12 | 10 | 12 | -2 | 25
13 | 10 | 12 | -2 | 25
14 | 10 | 10 | 0 | 25
15 | 10 | 11 | -1 | 25
16 | 10 | 11 | -1 | 25
17 | no campers |  | #VALUE!
18 | no campers |  | #VALUE!
19 | 10 | 11 | -1 | 25
20 | 10 | 11 | -1 | 25
21 | 10 | 11 | -1 | 25
22 | 10 | 11 | -1 | 25 | 1.33 | 1.42
23 | 10 | 11 | -1 | 25 | 0.66 | 0.68
24 | 10 | 11 | -1 | 25 | 0.65 | 0.66
25 | 10 | 11 | -1 | 25 | 0.6 | 0.64
26 | 10 | 11 | -1 | 25 | 0.31 | 0.4
27 | 10 | 11 | -1 | 25 | 0.34 | 0.44
28 | 10 | 11 | -1 | 25 | 0.45 | 0.58
29 | 10 | 11 | -1 | 25 | 0.29 | 0.36
30 | 10 | 11 | -1 | 25 | 1.16 | 1.28
31 | no | campers | #VALUE!
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Rob Wright
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2021-08-12
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )822 3511 |  | CERT #: 4191783
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | White Branch Youth Camp |  | ID#: 41 | 91783 | Month/Year: | 2021-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.6 | 26 | 41.6 | 15 | 7.2 | 31.4146 | YES
2 | 1.6 | 25 | 40 | 15 | 7.2 | 31.4146 | YES
3 | no campers |  | #VALUE! |  |  | #VALUE! | #VALUE!
4 | 1.8 | 26 | 46.8 | 16 | 7.3 | 31.1994 | YES
5 | 1.5 | 26 | 39 | 16 | 7.1 | 27.9938 | YES
6 | 1.9 | 26 | 49.4 | 16 | 7.3 | 31.5567 | YES
7 | 1.2 | 26 | 31.2 | 16.3 | 7.4 | 29.6379 | YES
8 | 1.2 | 26 | 31.2 | 16 | 7.3 | 29.1366 | YES
9 | 1.3 | 26 | 33.8 | 16.1 | 7.4 | 30.3808 | YES
10 | no campers |  | #VALUE! |  |  | #VALUE! | #VALUE!
11 | no campers |  | #VALUE! |  |  | #VALUE! | #VALUE!
12 | 1.3 | 26 | 33.8 | 16.4 | 7.4 | 29.7784 | YES
13 | 1.2 | 26 | 31.2 | 16.5 | 7.4 | 29.2446 | YES
14 | 1.1 | 26 | 28.6 | 16.7 | 7.4 | 28.5288 | YES
15 | 1.1 | 26 | 28.6 | 16.7 | 7.4 | 28.5288 | YES
16 | 1.1 | 26 | 28.6 | 16.7 | 7.3 | 27.4883 | YES
17 | no campers |  | #VALUE! |  |  | #VALUE! | #VALUE!
18 | no campers |  | #VALUE! |  |  | #VALUE! | #VALUE!
19 | 3.2 | 26 | 83.2 | 16.7 | 7.4 | 36.2321 | YES
20 | 3 | 26 | 78 | 16.8 | 7.4 | 35.1839 | YES
21 | 3.1 | 26 | 80.6 | 16.9 | 7.4 | 35.3499 | YES
22 | 3.2 | 26 | 83.2 | 16.8 | 7.4 | 35.9921 | YES
23 | 1.5 | 26 | 39 | 16.7 | 7.3 | 28.7734 | YES
24 | 1.2 | 26 | 31.2 | 16.7 | 7.4 | 28.8563 | YES
25 | 1.2 | 26 | 31.2 | 16.6 | 7.3 | 27.9909 | YES
26 | 1.4 | 26 | 36.4 | 16.9 | 7.4 | 29.1306 | YES
27 | 1.2 | 26 | 31.2 | 17 | 7.4 | 28.2833 | YES
28 | 3 | 26 | 78 | 18 | 7.4 | 32.4826 | YES
29 | 1.2 | 26 | 31.2 | 18.1 | 7.5 | 27.2712 | YES
30 | 4 | 26 | 104 | 17.4 | 7 | 32.6696 | YES
31 | no campers |  | #VALUE! |  |  | #VALUE! | #VALUE!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2