## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | White Branch Youth Camp |  |  | ID#: 41 | 91783 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 10 | 11 | -1 | 25 | 0.37 | 0.49
2 | 10 | 11 | -1 | 25 | 0.38 | 0.45
3 | 10 | 10 | 0 | 25 | 0.62 | 0.67
4 | 10 | 10 | 0 | 25 | 0.42 | 0.5
5 | 10 | 10 | 0 | 25 | 0.42 | 0.56
6 | 10 | 10 | 0 | 25 | 0.46 | 0.57
7 | 10 | 10 | 0 | 25 | 0.26 | 0.38
8 | 10 | 10 | 0 | 25 | 0.5 | 0.55
9 | 10 | 10 | 0 | 25 | 1.34 | 1.54
10 | 10 | 10 | 0 | 25 | 1.15 | 1.5
11 | 10 | 10 | 0 | 25 | 0.55 | 0.6
12 | 10 | 10 | 0 | 25 | 0.52 | 0.6
13 | 10 | 10 | 0 | 25 | 0.44 | 0.5
14 | 10 | 10 | 0 | 25 | 0.37 | 0.51
15 | 10 | 10 | 0 | 25 | 0.39 | 0.57
16 | 10 | 10 | 0 | 25 | 0.49 | 0.61
17 | 10 | 10 | 0 | 25 | 0.51 | 0.58
18 | 10 | 10 | 0 | 25 | 0.54 | 0.59
19 | NO CAMPER | NO CAMPER | #VALUE! | 25 | NO CAMPER | NO CAMPERS
20 | 10 | 10 | 0 | 25 | 0.74 | 0.79
21 | 10 | 10 | 0 | 25 | 1.63 | 1.68
22 | 10 | 10 | 0 | 25 | 1.66 | 1.72
23 | no camper |  | #VALUE! | 25 |  | NO CAMPERS
24 | no camper |  | #VALUE! | 25 |  | NO CAMPERS
25 | no camper |  | #VALUE! | 25 |  | NO CAMPERS
26 | no camper |  | #VALUE! | 25 |  | no campers
27 | no camper |  | #VALUE! | 25 |  | no campers
28 | no camper |  | #VALUE! | 25 |  | no campers
29 | no camper |  | #VALUE! | 25 |  | no campers
30 | no camper |  | #VALUE! | 25 |  | no campers
31 | no camper |  | #VALUE! | 25 |  | no campers
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | no | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Rob Wright
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Rob Wright |  | DATE: 8/25/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )822-3511 |  | CERT #:4191783
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | White Branch Youth Camp |  | ID#: 41 | 91783 | Month/Year: | 2021-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 26 | 31.2 | 17.6 | 7.5 | 28.1991 | YES
2 | 1.2 | 26 | 31.2 | 17.9 | 7.4 | 26.6298 | YES
3 | 3 | 26 | 78 | 17.7 | 7.2 | 30.7732 | YES
4 | 1.2 | 25 | 30 | 17.6 | 7.5 | 28.1991 | YES
5 | 1.2 | 26 | 31.2 | 17.5 | 7.5 | 28.3883 | YES
6 | 1.2 | 26 | 31.2 | 17.4 | 7.5 | 28.5787 | YES
7 | 1.2 | 26 | 31.2 | 17 | 7.4 | 28.2833 | YES
8 | 3 | 26 | 78 | 18 | 7.3 | 31.3 | YES
9 | 3.2 | 26 | 83.2 | 17.5 | 7.4 | 34.3548 | YES
10 | 2.6 | 26 | 67.6 | 17.1 | 7.5 | 34.1969 | YES
11 | 2.5 | 26 | 65 | 17.5 | 7.5 | 32.9217 | YES
12 | 2.5 | 26 | 65 | 17.8 | 7.4 | 31.0971 | YES
13 | 2.4 | 26 | 62.4 | 18 | 7.5 | 31.4823 | YES
14 | 2.5 | 26 | 65 | 18.1 | 7.4 | 30.5 | YES
15 | 2.9 | 26 | 75.4 | 18.4 | 7.5 | 32.4493 | YES
16 | 2.8 | 26 | 72.8 | 18.4 | 7.5 | 32.0821 | YES
17 | 2.6 | 26 | 67.6 | 18.4 | 7.5 | 31.3598 | YES
18 | 2.1 | 26 | 54.6 | 18.1 | 7.7 | 32.546 | YES
19 | no camper | 26 | no camper | no camper | 7.5 | no camper | no camper
20 | 1.2 | 26 | 31.2 | 17.3 | 7.4 | 27.7214 | YES
21 | 1.3 | 26 | 33.8 | 17 | 7.5 | 29.6898 | YES
22 | 1.6 | 26 | 41.6 | 17.3 | 7.5 | 30.1137 | YES
23 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
24 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
25 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
26 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
27 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
28 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
29 | no camper | 26 | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
30 | no camper |  | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
31 | no camper |  | #VALUE! | no camper | no camper | #VALUE! | #VALUE!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2