## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-06-01
System Name: | WHITE BRANCH YOUTH CAMP |  |  | ID#: 41 | 91783 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 27 | 27 | 0 | 25 | 0.15 | 0.16
2 | 27 | 27 | 0 | 25 | 0.22 | 0.22
3 | no campers |  | #VALUE! | 25
4 | 27 | 27 | 0 | 25 | 0.25 | 0.26
5 | 27 | 27 | 0 | 25 | 0.29 | 0.29
6 | 27 | 27 | 0 | 25 | 0.26 | 0.27
7 | no campers |  | #VALUE! | 25
8 | no campers |  | #VALUE! | 25
9 | 27 | 27 | 0 | 25 | 0.27 | 0.28
10 | 27 | 27 | 0 | 25 | 0.31 | 0.33
11 | 27 | 27 | 0 | 25 | 0.27 | 0.31
12 | 27 | 27 | 0 | 25 | 0.26 | 0.29
13 | no camper |  | #VALUE! | 25
14 | 27 | 27 | 0 | 25 | 0.26 | 0.3
15 | 27 | 27 | 0 | 25 | 0.29 | 0.33
16 | no camper |  | #VALUE! | 25
17 | no camper |  | #VALUE! | 25
18 | no camper |  | #VALUE! | 25
19 | no camper |  | #VALUE! | 25
20 | 27 | 27 | 0 | 25 | 0.39 | 0.44
21 | 27 | 27 | 0 | 25 | 0.4 | 0.44
22 | 27 | 27 | 0 | 25 | 0.22 | 0.24
23 | 27 | 27 | 0 | 25 | 0.23 | 0.27
24 | 27 | 27 | 0 | 25 | 0.26 | 0.26
25 | no campers |  | #VALUE! | 25
26 | no campers |  | #VALUE! | 25
27 | 21 | 21 | 0 | 25 | 0.17 | 0.18
28 | 21 | 21 | 0 | 25 | 0.2 | 0.21
29 | 21 | 21 | 0 | 25 | 0.16 | 0.18
30 | 21 | 21 | 0 | 25 | 0.13 | 0.18
31 | N/A
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Tiffany Kingsley
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Tiffany Kingsley |  | DATE: 7.1.24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 854-0441 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.9 | 26 | 75.4 | 10.8 | 7.5 | 54.1527 | YES
2 | 2.2 | 26 | 57.2 | 11 | 7.7 | 52.9544 | YES
3 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
4 | 2.8 | 26 | 72.8 | 11 | 7.7 | 56.7486 | YES
5 | 2.5 | 26 | 65 | 11 | 7.8 | 56.8222 | YES
6 | 1.8 | 26 | 46.8 | 11.2 | 7.5 | 46.4885 | YES
7 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
8 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
9 | 2.5 | 26 | 65 | 13 | 7.6 | 46.0465 | YES
10 | 2.3 | 26 | 59.8 | 13.1 | 7.7 | 46.3946 | YES
11 | 2.5 | 26 | 65 | 13.6 | 7.7 | 45.9108 | YES
12 | 2.5 | 26 | 65 | 14 | 7.7 | 44.7116 | YES
13 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
14 | 2.3 | 26 | 59.8 | 14 | 7.6 | 42.1332 | YES
15 | 2.8 | 26 | 72.8 | 13 | 7.5 | 45.9155 | YES
16 | no camper | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
17 | no camper | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
18 | no camper | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
19 | no camper | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
20 | 2.9 | 26 | 75.4 | 12.1 | 7.6 | 51.4343 | YES
21 | 2.9 | 26 | 75.4 | 12.2 | 7.6 | 51.091 | YES
22 | 2.9 | 26 | 75.4 | 13.6 | 7.7 | 48.0322 | YES
23 | 2 | 26 | 52 | 13.5 | 7.7 | 43.6764 | YES
24 | 1.8 | 26 | 46.8 | 13.1 | 7.7 | 43.8458 | YES
25 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
26 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
27 | 2 | 26 | 52 | 13.7 | 7.7 | 43.1017 | YES
28 | 1.7 | 26 | 44.2 | 14 | 7.5 | 37.9412 | YES
29 | 1.7 | 26 | 44.2 | 14.6 | 7.7 | 39.2496 | YES
30 | 1.7 | 26 | 44.2 | 14.6 | 7.6 | 37.829 | YES
31 | N/A |  | #VALUE! |  |  | #VALUE! | #VALUE!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: DWP.DMCE@odhsoha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2