## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-01
System Name: | WHITE BRANCH YOUTH CAMP |  |  | ID#: 41 | 91783 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 27 | 26 | 1 | 25 | 0.09 | 0.12
2 | 27 | 26 | 1 | 25 | 0.07 | 0.07
3 | 27 | 26 | 1 | 25 | 0.14 | 0.16
4 | 27 | 26 | 1 | 25 | 0.09 | 0.1
5 | 27 | 26 | 1 | 25 | 0.09 | 0.1
6 | 27 | 26 | 1 | 25 | 0.09 | 0.13
7 | 27 | 26 | 1 | 25 | 0.08 | 0.13
8 | 27 | 26 | 1 | 25 | 0.07 | 0.13
9 | 27 | 26 | 1 | 25 | 0.07 | 0.08
10 | 27 | 26 | 1 | 25 | 0.07 | 0.12
11 | 27 | 26 | 1 | 25 | 0.07 | 0.1
12 | no campers |  | #VALUE! | 25
13 | no campers |  | #VALUE! | 25
14 | no campers |  | #VALUE! | 25
15 | 27 | 26 | 1 | 25 | 0.22 | 0.25
16 | 27 | 26 | 1 | 25 | 0.12 | 0.14
17 | 27 | 26 | 1 | 25 | 0.12 | 0.14
18 | 27 | 26 | 1 | 25 | 0.13 | 0.14
19 | no campers |  | #VALUE! | 25
20 | no campers |  | #VALUE! | 25
21 | 27 | 26 | 1 | 25 | 0.013 | 0.15
22 | no campers |  | #VALUE! | 25
23 | 27 | 26 | 1 | 25 | 0.19 | 0.19
24 | 27 | 26 | 1 | 25 | 0.21 | 0.25
25 | 27 | 26 | 1 | 25 | 0.16 | 0.24
26 | no campers |  | #VALUE! | 25
27 | no campers |  | #VALUE! | 25
28 | no campers |  | #VALUE! | 25
29 | no campers |  | #VALUE! | 25
30 | no campers |  | #VALUE! | 25
31 | no campers |  | #VALUE! | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | YES | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES | YES
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: TIFFANY KINGSLEY
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Tiffany Kingsley |  | DATE: 9.3.24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 854-0441 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.3 | 26 | 33.8 | 19 | 7.5 | 25.9709 | YES
2 | 1.3 | 26 | 33.8 | 19.6 | 7.5 | 24.9463 | YES
3 | 1.5 | 26 | 39 | 17.2 | 7.5 | 29.9717 | YES
4 | 1.5 | 26 | 39 | 17 | 7.5 | 30.3746 | YES
5 | 1.8 | 26 | 46.8 | 17.6 | 7.6 | 31.3373 | YES
6 | 1.8 | 26 | 46.8 | 16.2 | 7.5 | 33.1519 | YES
7 | 1.8 | 26 | 46.8 | 16.7 | 7.6 | 33.2744 | YES
8 | 2 | 26 | 52 | 16.6 | 7.5 | 33.0231 | YES
9 | 1.1 | 26 | 28.6 | 17.9 | 7.6 | 28.3591 | YES
10 | 1.5 | 26 | 39 | 17 | 7.6 | 31.5211 | YES
11 | 1.6 | 26 | 41.6 | 17 | 7.6 | 31.8821 | YES
12 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
13 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
14 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
15 | 1.8 | 26 | 46.8 | 16.8 | 7.6 | 33.0535 | YES
16 | 2 | 26 | 52 | 15.7 | 7.5 | 35.0617 | YES
17 | 1.8 | 26 | 46.8 | 16.5 | 7.5 | 32.4959 | YES
18 | 1.6 | 26 | 41.6 | 16 | 7.6 | 34.0781 | YES
19 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
20 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
21 | 1.3 | 26 | 33.8 | 15.8 | 7.5 | 32.1645 | YES
22 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
23 | 2 | 26 | 52 | 15 | 7.5 | 36.7319 | YES
24 | 2 | 26 | 52 | 15 | 7.6 | 38.1121 | YES
25 | 2 | 26 | 52 | 14.4 | 7.6 | 39.6603 | YES
26 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
27 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
28 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
29 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
30 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
31 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: DWP.DMCE@odhsoha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2