## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-09-01
System Name: | WHITE BRANCH YOUTH CAMP |  |  | ID#: 41 | 91783 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | no campers |  | #VALUE! | 25
2 | no campers |  | #VALUE! | 25
3 | no campers |  | #VALUE! | 25
4 | 27 | 26 | 1 | 25 | 0.22 | 0.24
5 | 27 | 26 | 1 | 25 | 0.08 | 0.09
6 | 27 | 26 | 1 | 25 | 0.07 | 0.08
7 | no campers |  | #VALUE! | 25
8 | no campers |  | #VALUE! | 25
9 | no campers |  | #VALUE! | 25
10 | no campers |  | #VALUE! | 25
11 | no campers |  | #VALUE! | 25
12 | no campers |  | #VALUE! | 25
13 | no campers |  | #VALUE! | 25
14 | no campers |  | #VALUE! | 25
15 | no campers |  | #VALUE! | 25
16 | no campers |  | #VALUE! | 25
17 | no campers |  | #VALUE! | 25
18 | no campers |  | #VALUE! | 25
19 | no campers |  | #VALUE! | 25
20 | 27 | 26 | 1 | 25 | 0.43 | 0.44
21 | 27 | 26 | 1 | 25 | 0.21 | 0.23
22 | 27 | 26 | 1 | 25 | 0.14 | 0.14
23 | no campers |  | #VALUE! | 25
24 | no campers |  | #VALUE! | 25
25 | no campers |  | #VALUE! | 25
26 | 26 | 24 | 2 | 25 | 0.26 | 0.27
27 | 26 | 24 | 2 | 25 | 0.19 | 0.21
28 | 26 | 24 | 2 | 25 | 0.19 | 0.19
29 | 26 | 24 | 2 | 25 | 0.47 | 0.56
30 | no campers |  | #VALUE! | 25
31 | NA | NA | #VALUE! | NA | NA | NA
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | YES | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES | YES
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: TIFFANY KINGSLEY
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Tiffany Kingsley |  | DATE: 10.1.24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 854-0441 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
2 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
3 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
4 | 2 | 26 | 52 | 15.3 | 7.6 | 37.3604 | YES
5 | 2 | 26 | 52 | 14.9 | 7.6 | 38.366 | YES
6 | 2.4 | 26 | 62.4 | 15.6 | 7.6 | 38.3229 | YES
7 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
8 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
9 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
10 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
11 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
12 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
13 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
14 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
15 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
16 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
17 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
18 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
19 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
20 | 2.5 | 26 | 65 | 14.2 | 7.5 | 40.9932 | YES
21 | 2 | 26 | 52 | 14.1 | 7.6 | 40.4574 | YES
22 | 2 | 26 | 52 | 13.5 | 7.6 | 42.0988 | YES
23 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
24 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
25 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
26 | 2 | 26 | 52 | 14.5 | 7.5 | 37.9722 | YES
27 | 2 | 26 | 52 | 13.1 | 7.5 | 41.6676 | YES
28 | 2 | 26 | 52 | 13.9 | 7.5 | 39.5149 | YES
29 | 2 | 26 | 52 | 13.3 | 7.6 | 42.6604 | YES
30 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
31 | NA | NS | #VALUE! | NA | NA | #VALUE! | #VALUE! | NA
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: DWP.DMCE@odhsoha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2