## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-01-01
System Name: | WHITE BRANCH YOUTH CAMP |  |  | ID#: 41 | 91783 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | no campers |  | #VALUE! | 25
2 | 27 | 26 | 1 | 25 | 0.46 | 0.46
3 | 27 | 26 | 1 | 25 | 0.63 | 0.63
4 | 27 | 26 | 1 | 25 | 0.76 | 0.76
5 | 27 | 26 | 1 | 25 | 0.87 | 0.87
6 | no campers |  | #VALUE! | 25
7 | no campers |  | #VALUE! | 25
8 | no campers |  | #VALUE! | 25
9 | no campers |  | #VALUE! | 25
10 | no campers |  | #VALUE! | 25
11 | no campers |  | #VALUE! | 25
12 | no campers |  | #VALUE! | 25
13 | 27 | 26 | 1 | 25 | 0.36 | 0.42
14 | no campers |  | #VALUE! | 25
15 | no campers |  | #VALUE! | 25
16 | no campers |  | #VALUE! | 25
17 | 27 | 26 | 1 | 25 | 0.4 | 0.41
18 | 27 | 26 | 1 | 25 | 0.44 | 0.46
19 | 27 | 26 | 1 | 25 | 0.43 | 0.47
20 | 27 | 26 | 1 | 25 | 0.35 | 0.4
21 | no |  | #VALUE! | 25
22 | no campers |  | #VALUE! | 25
23 | no campers |  | #VALUE! | 25
24 | 27 | 24 | 3 | 25 | 0.5 | 0.53
25 | 27 | 24 | 3 | 25 | 0.4 | 0.43
26 | no campers |  | #VALUE! | 25
27 | no campers |  | #VALUE! | 25
28 | no campers |  | #VALUE! | 25
29 | no campers |  | #VALUE! | 25
30 | no campers |  | #VALUE! | 25
31 | no campers |  | #VALUE! | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | YES | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES | YES
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: TIFFANY KINGSLEY
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Tiffany Kingsley |  | DATE: 2/1/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 854-0441 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
2 | 4 | 26 | 104 | 3.6 | 7.5 | 101.1123 | YES
3 | 4 | 26 | 104 | 3.8 | 7.5 | 99.7082 | YES
4 | 4 | 26 | 104 | 3.6 | 7.5 | 101.1123 | YES
5 | 4 | 26 | 104 | 4 | 7.5 | 98.3244 | YES
6 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
7 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
8 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
9 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
10 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
11 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
12 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
13 | 4 | 26 | 104 | 3.8 | 7.5 | 99.7082 | YES
14 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
15 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
16 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
17 | 4.5 | 26 | 117 | 2.8 | 7.5 | 113.5618 | YES
18 | 4.5 | 26 | 117 | 2.6 | 7.5 | 115.1696 | YES
19 | 4.5 | 26 | 117 | 2.4 | 7.5 | 116.8011 | YES
20 | 4.5 | 26 | 117 | 2.7 | 7.5 | 114.3628 | YES
21 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
22 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
23 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
24 | 5 | 26 | 130 | 2.1 | 7.5 | 126.7138 | YES
25 | 5 | 26 | 130 | 2.2 | 7.5 | 125.823 | YES
26 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
27 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
28 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
29 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
30 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
31 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: DWP.DMCE@odhsoha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2