## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | WHITE BRANCH YOUTH CAMP |  |  | ID#: 41 | 91783 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 27 | 25 | 2 | 25 | 0.4 | 0.4
2 | 27 | 25 | 2 | 25 | 0.29 | 0.3
3 | 27 | 25 | 2 | 25 | 0.34 | 0.34
4 | 27 | 25 | 2 | 25 | 0.23 | 0.23
5 | 27 | 25 | 2 | 25 | 0.2 | 0.22
6 | 27 | 25 | 2 | 25 | 0.19 | 0.19
7 | 27 | 25 | 2 | 25 | 0.43 | 0.45
8 | 27 | 25 | 2 | 25 | 0.28 | 0.28
9 | 27 | 25 | 2 | 25 | 0.21 | 0.24
10 | 27 | 25 | 2 | 25 | 0.28 | 0.32
11 | no campers |  | #VALUE! | 25
12 | no campers |  | #VALUE! | 25
13 | no campers |  | #VALUE! | 25
14 | 27 | 25 | 2 | 25 | 0.23 | 0.23
15 | 27 | 25 | 2 | 25 | 0.23 | 0.23
16 | 27 | 25 | 2 | 25 | 0.19 | 0.2
17 | 27 | 25 | 2 | 25 | 0.15 | 0.17
18 | no campers |  | #VALUE! | 25
19 | no campers |  | #VALUE! | 25
20 | no campers |  | #VALUE! | 25
21 | no campers |  | #VALUE! | 25
22 | 27 | 25 | 2 | 25 | 0.16 | 0.18
23 | 27 | 25 | 2 | 25 | 0.2 | 0.21
24 | 27 | 25 | 2 | 25 | 0.21 | 0.23
25 | no campers |  | #VALUE! | 25
26 | no campers |  | #VALUE! | 25
27 | no campers |  | #VALUE! | 25
28 | no campers |  | #VALUE! | 25
29 | no campers |  | #VALUE! | 25
30 | no campers |  | #VALUE! | 25
31 | no campers |  | #VALUE! | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | YES | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES | YES
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: TIFFANY KINGSLEY
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Tiffany Kingsley |  | DATE: 9/2/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 854-0441 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | WHITE BRANCH YOUTH CAMP |  | ID#: 41 | 91783 | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 26 | 52 | 17 | 7.6 | 33.3666 | YES
2 | 2 | 26 | 52 | 16.7 | 7.6 | 34.0397 | YES
3 | 2 | 26 | 52 | 16.8 | 7.6 | 33.8139 | YES
4 | 2 | 26 | 52 | 17.7 | 7.6 | 31.8461 | YES
5 | 2 | 26 | 52 | 16.2 | 7.6 | 35.1911 | YES
6 | 2 | 26 | 52 | 17.6 | 7.6 | 32.0591 | YES
7 | 2 | 26 | 52 | 15.8 | 7.6 | 36.1396 | YES
8 | 2 | 26 | 52 | 16 | 7.6 | 35.6623 | YES
9 | 2 | 26 | 52 | 16 | 7.6 | 35.6623 | YES
10 | 2 | 26 | 52 | 16.2 | 7.6 | 35.1911 | YES
11 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
12 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
13 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
14 | 2 | 26 | 52 | 17.8 | 7.6 | 31.6345 | YES
15 | 2 | 26 | 52 | 17.8 | 7.6 | 31.6345 | YES
16 | 2 | 26 | 52 | 18 | 7.6 | 31.2154 | YES
17 | 2 | 26 | 52 | 18.6 | 7.6 | 29.9902 | YES
18 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
19 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
20 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
21 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
22 | 2 | 26 | 52 | 17.5 | 7.6 | 32.2735 | YES
23 | 2 | 26 | 52 | 17.1 | 7.6 | 33.1451 | YES
24 | 2 | 26 | 52 | 17.3 | 7.6 | 32.7065 | YES
25 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
26 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
27 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
28 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
29 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
30 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
31 | no campers | 26 | #VALUE! |  |  | #VALUE! | #VALUE!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: DWP.DMCE@odhsoha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2