## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-03-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.34 | 0.33 | 0.32 | 0.34 | 0.34
2 |  |  | 0.31 | 0.32 | 0.32 | 0.36 | 0.36
3 |  |  | 0.33 | 0.34 | 0.32 | 0.34 | 0.34
4 |  |  | 0.36 | 0.31 | 0.32 | 0.36 | 0.36
5 |  |  | 0.36 | 0.38 | 0.35 | 0.38 | 0.38
6 |  |  | 0.35 | 0.31 | 0.32 | 0.36 | 0.36
7 |  |  | 0.29 | 0.33 | 0.31 | 0.35 | 0.35
8 |  |  | 0.33 | 0.33 | 0.31 | 0.33 | 0.33
9 |  |  | 0.32 | 0.32 | 0.31 | 0.34 | 0.34
10 |  |  | 0.32 | 0.32 | 0.33 | 0.33 | 0.33
11 |  |  | 0.32 | 0.34 | 0.35 | 0.35 | 0.35
12 |  |  | 0.38 | 0.35 | 0.37 | 0.38 | 0.38
13 |  |  | 0.32 | 0.33 | 0.33 | 0.34 | 0.34
14 |  |  | 0.4 | 0.41 | 0.39 | 0.41 | 0.41
15 |  |  | 0.35 | 0.37 | 0.37 | 0.37 | 0.37
16 |  |  | 0.35 | 0.34 | 0.32 | 0.36 | 0.36
17 |  |  | 0.38 | 0.36 | 0.39 | 0.39 | 0.39
18 |  |  | 0.34 | 0.35 | 0.35 | 0.36 | 0.36
19 |  |  | 0.37 | 0.35 | 0.34 | 0.37 | 0.37
20 |  |  | 0.35 | 0.35 | 0.34 | 0.35 | 0.35
21 |  |  | 0.39 | 0.39 | 0.4 | 0.41 | 0.41
22 |  |  | 0.37 | 0.35 | 0.36 | 0.38 | 0.38
23 |  |  | 0.4 | 0.4 | 0.39 | 0.4 | 0.4
24 |  |  | 0.42 | 0.41 | 0.42 | 0.42 | 0.42
25 |  |  | 0.42 | 0.41 | 0.41 | 0.42 | 0.42
26 |  |  | 0.39 | 0.37 | 0.38 | 0.4 | 0.4
27 |  |  | 0.38 | 0.37 | 0.39 | 0.39 | 0.39
28 |  |  | 0.4 | 0.41 | 0.39 | 0.41 | 0.41
29 |  |  | 0.39 | 0.38 | 0.4 | 0.4 | 0.4
30 |  |  | 0.41 | 0.41 | 0.41 | 0.41 | 0.41
31 |  |  | 0.39 | 0.38 | 0.38 | 0.39 | 0.39
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:4/5/2021
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.5 | 50 | 125 | 13.6 | 7.6 | 44.254 | yes | 7
2 | 2.4 | 50 | 120 | 13.6 | 7.6 | 43.7565 | yes | 7
3 | 2.5 | 50 | 125 | 13.8 | 7.6 | 43.6719 | yes | 7
4 | 2.5 | 50 | 125 | 14 | 7.6 | 43.0973 | yes | 7
5 | 2.4 | 50 | 120 | 14 | 7.6 | 42.6126 | yes | 7
6 | 2.5 | 50 | 125 | 14 | 7.6 | 43.0973 | yes | 7
7 | 2.5 | 50 | 125 | 14.2 | 7.6 | 42.5301 | yes | 7
8 | 2.5 | 50 | 125 | 14 | 7.7 | 44.7116 | yes | 7
9 | 2.5 | 50 | 125 | 14.1 | 7.6 | 42.8128 | yes | 7
10 | 2.4 | 50 | 120 | 14 | 7.6 | 42.6126 | yes | 7
11 | 2.5 | 50 | 125 | 14.4 | 7.6 | 41.9703 | yes | 7
12 | 2.5 | 50 | 125 | 14.1 | 7.6 | 42.8128 | yes | 7
13 | 2.5 | 50 | 125 | 14.5 | 7.6 | 41.6931 | yes | 7
14 | 2.5 | 50 | 125 | 14.2 | 7.6 | 42.5301 | yes | 7
15 | 2.5 | 50 | 125 | 14.7 | 7.6 | 41.144 | yes | 7
16 | 2.5 | 50 | 125 | 14.6 | 7.6 | 41.4177 | yes | 7
17 | 2.6 | 50 | 130 | 14.6 | 7.6 | 41.8891 | yes | 7
18 | 2.5 | 50 | 125 | 14.8 | 7.5 | 39.3941 | yes | 7
19 | 2.6 | 50 | 130 | 15 | 7.6 | 40.793 | yes | 7
20 | 2.5 | 50 | 125 | 15.2 | 7.6 | 39.8022 | yes | 7
21 | 2.5 | 50 | 125 | 14.9 | 7.6 | 40.6021 | yes | 7
22 | 2.5 | 50 | 125 | 14.6 | 7.6 | 41.4177 | yes | 7
23 | 2.5 | 50 | 125 | 14.6 | 7.6 | 41.4177 | yes | 7
24 | 2.5 | 50 | 125 | 14.7 | 7.6 | 41.144 | yes | 7
25 | 2.5 | 50 | 125 | 14.3 | 7.6 | 42.2493 | yes | 7
26 | 2.4 | 50 | 120 | 14.6 | 7.6 | 40.9515 | yes | 7
27 | 2.5 | 50 | 125 | 14.4 | 7.6 | 41.9703 | yes | 7
28 | 2.6 | 50 | 130 | 14.6 | 7.6 | 41.8891 | yes | 7
29 | 2.6 | 50 | 130 | 15.1 | 7.6 | 40.5235 | yes | 7
30 | 2.5 | 50 | 125 | 14.6 | 7.6 | 41.4177 | yes | 7
31 | 2.5 | 50 | 125 | 14.4 | 7.6 | 41.9703 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2