## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-05-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.45 | 0.48 | 0.51 | 0.63 | 0.63
2 |  |  | 0.44 | 0.42 | 0.39 | 0.44 | 0.44
3 |  |  | 0.46 | 0.44 | 0.45 | 0.46 | 0.46
4 |  |  | 0.45 | 0.39 | 0.42 | 0.45 | 0.45
5 |  |  | 0.36 | 0.34 | 0.35 | 0.39 | 0.39
6 |  |  | 0.39 | 0.41 | 0.41 | 0.41 | 0.41
7 |  |  | 0.43 | 0.42 | 0.41 | 0.44 | 0.44
8 |  |  | 0.35 | 0.38 | 0.36 | 0.38 | 0.38
9 |  |  | 0.36 | 0.36 | 0.35 | 0.36 | 0.36
10 |  |  | 0.38 | 0.38 | 0.41 | 0.41 | 0.41
11 |  |  | 0.42 | 0.43 | 0.41 | 0.43 | 0.43
12 |  |  | 0.4 | 0.4 | 0.4 | 0.41 | 0.41
13 |  |  | 0.39 | 0.41 | 0.38 | 0.43 | 0.43
14 |  |  | 0.39 | 0.4 | 0.38 | 0.4 | 0.4
15 |  |  | 0.36 | 0.39 | 0.39 | 0.39 | 0.39
16 |  |  | 0.33 | 0.33 | 0.34 | 0.34 | 0.34
17 |  |  | 0.35 | 0.33 | 0.33 | 0.38 | 0.38
18 |  |  | 0.33 | 0.33 | 0.32 | 0.34 | 0.34
19 |  |  | 0.35 | 0.36 | 0.35 | 0.36 | 0.36
20 |  |  | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
21 |  |  | 0.36 | 0.34 | 0.35 | 0.36 | 0.36
22 |  |  | 0.37 | 0.38 | 0.36 | 0.38 | 0.38
23 |  |  | 0.3 | 0.42 | 0.42 | 0.42 | 0.42
24 |  |  | 0.41 | ..42 | 0.4 | 0.42 | 0.42
25 |  |  | 0.48 | 0.45 | 0.48 | 0.51 | 0.51
26 |  |  | 0.47 | 0.46 | 0.43 | 0.48 | 0.48
27 |  |  | 0.44 | 0.45 | 0.46 | 0.46 | 0.46
28 |  |  | 0.48 | 0.46 | 0.47 | 0.49 | 0.49
29 |  |  | 0.45 | 0.44 | 0.43 | 0.45 | 0.45
30 |  |  | 0.43 | 0.39 | 0.38 | 0.44 | 0.44
31 |  |  | 0.43 | 0.46 | 0.46 | 0.47 | 0.47
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:6/5/2021
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.4 | 50 | 120 | 19.4 | 7.7 | 30.8808 | yes | 7
2 | 2.4 | 50 | 120 | 19.4 | 7.7 | 30.8808 | yes | 7
3 | 2.4 | 50 | 120 | 19.5 | 7.7 | 30.6754 | yes | 7
4 | 2.4 | 50 | 120 | 20.1 | 7.7 | 29.4709 | yes | 7
5 | 2.5 | 50 | 125 | 20.4 | 7.7 | 29.2176 | yes | 7
6 | 2.5 | 50 | 125 | 20 | 7.7 | 30.0087 | yes | 7
7 | 2.4 | 50 | 120 | 20.1 | 7.7 | 29.4709 | yes | 7
8 | 2.4 | 50 | 120 | 19.8 | 7.7 | 30.0673 | yes | 7
9 | 2.4 | 50 | 120 | 19.6 | 7.7 | 30.4714 | yes | 7
10 | 2.5 | 50 | 125 | 20 | 7.7 | 30.0087 | yes | 7
11 | 2.4 | 50 | 120 | 20.1 | 7.7 | 29.4709 | yes | 7
12 | 2.5 | 50 | 125 | 20 | 7.7 | 30.0087 | yes | 7
13 | 2.5 | 50 | 125 | 20.1 | 7.7 | 29.809 | yes | 7
14 | 2.4 | 50 | 120 | 20 | 7.7 | 29.6684 | yes | 7
15 | 2.5 | 50 | 125 | 20.2 | 7.7 | 29.6105 | yes | 7
16 | 2.5 | 50 | 125 | 20.1 | 7.7 | 29.809 | yes | 7
17 | 2.5 | 50 | 125 | 20 | 7.7 | 30.0087 | yes | 7
18 | 2.4 | 50 | 120 | 19.8 | 7.7 | 30.0673 | yes | 7
19 | 2.5 | 50 | 125 | 19.6 | 7.7 | 30.8206 | yes | 7
20 | 2.4 | 50 | 120 | 19 | 7.7 | 31.7157 | yes | 7
21 | 2.4 | 50 | 120 | 18.9 | 7.7 | 31.9279 | yes | 7
22 | 2.5 | 50 | 125 | 18.6 | 7.7 | 32.9453 | yes | 7
23 | 2.5 | 50 | 125 | 18.8 | 7.7 | 32.5093 | yes | 7
24 | 2.4 | 50 | 120 | 18.4 | 7.7 | 33.0095 | yes | 7
25 | 2.4 | 50 | 120 | 18.6 | 7.7 | 32.5727 | yes | 7
26 | 2.5 | 50 | 125 | 18.8 | 7.7 | 32.5093 | yes | 7
27 | 2.5 | 50 | 125 | 18.6 | 7.7 | 32.9453 | yes | 7
28 | 2.4 | 50 | 120 | 18.4 | 7.7 | 33.0095 | yes | 7
29 | 2.4 | 50 | 120 | 18.6 | 7.7 | 32.5727 | yes | 7
30 | 2.4 | 50 | 120 | 18.8 | 7.7 | 32.1414 | yes | 7
31 | 2.4 | 50 | 120 | 19.1 | 7.7 | 31.505 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2