## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-09-03
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.29 | 0.27 | 0.29 | 0.3 | 0.3
2 |  |  | 0.26 | 0.27 | 0.26 | 0.27 | 0.27
3 |  |  | 0.24 | 0.25 | 0.24 | 0.26 | 0.26
4 |  |  | 0.22 | 0.25 | 0.23 | 0.25 | 0.25
5 |  |  | 0.35 | 0.33 | 0.32 | 0.35 | 0.35
6 |  |  | 0.46 | 0.39 | 0.4 | 0.71 | 0.71
7 |  |  | 0.28 | 0.25 | 0.3 | 0.3 | 0.3
8 |  |  | 0.31 | 0.32 | 0.33 | 0.33 | 0.33
9 |  |  | 0.19 | 0.22 | 0.21 | 0.23 | 0.23
10 |  |  | 0.22 | 0.21 | 0.24 | 0.27 | 0.27
11 |  |  | 0.25 | 0.22 | 0.24 | 0.27 | 0.27
12 |  |  | 0.29 | 0.25 | 0.26 | 0.31 | 0.31
13 |  |  | 0.33 | 0.32 | 0.31 | 0.35 | 0.35
14 |  |  | 0.3 | 0.29 | 0.31 | 0.32 | 0.32
15 |  |  | 0.33 | 0.32 | 0.32 | 0.33 | 0.33
16 |  |  | 0.24 | 0.21 | 0.24 | 0.25 | 0.25
17 |  |  | 0.34 | 0.32 | 0.29 | 0.34 | 0.34
18 |  |  | 0.22 | 0.24 | 0.27 | 0.29 | 0.29
19 |  |  | 0.32 | 0.29 | 0.29 | 0.33 | 0.33
20 |  |  | 0.34 | 0.29 | 0.34 | 0.36 | 0.36
21 |  |  | 0.37 | 0.35 | 0.34 | 0.37 | 0.37
22 |  |  | 0.2 | 0.19 | 0.21 | 0.22 | 0.22
23 |  |  | 0.28 | 0.24 | 0.24 | 0.29 | 0.29
24 |  |  | 0.24 | 0.21 | 0.21 | 0.24 | 0.24
25 |  |  | 0.25 | 0.25 | 0.27 | 0.27 | 0.27
26 |  |  | 0.3 | 0.36 | 0.38 | 0.27 | 0.38
27 |  |  | 0.26 | 0.24 | 0.26 | 0.26 | 0.26
28 |  |  | 0.25 | 0.23 | 0.26 | 0.27 | 0.27
29 |  |  | 0.31 | 0.32 | 0.31 | 0.32 | 0.32
30 |  |  | 0.37 | 0.39 | 0.42 | 0.47 | 0.47
31 |  |  | 0 | 0 | 0 | 0 | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:10/3/2021
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.6 | 50 | 130 | 15.8 | 7.7 | 40.1367 | yes | 7
2 | 2.7 | 50 | 135 | 15.6 | 7.8 | 42.6778 | yes | 7
3 | 2.6 | 50 | 130 | 22.4 | 7.8 | 26.8309 | yes | 7
4 | 2.1 | 50 | 105 | 23.6 | 7.8 | 23.3758 | yes | 7
5 | 2.1 | 50 | 105 | 23.1 | 7.7 | 23.2889 | yes | 7
6 | 2.2 | 50 | 110 | 20.9 | 7.7 | 27.3049 | yes | 7
7 | 2.4 | 50 | 120 | 18.4 | 7.8 | 34.253 | yes | 7
8 | 2.5 | 50 | 125 | 24.4 | 7.7 | 22.3414 | yes | 7
9 | 2.5 | 50 | 125 | 23.1 | 7.7 | 24.3832 | yes | 7
10 | 2.5 | 50 | 125 | 23 | 7.8 | 25.4799 | yes | 7
11 | 2.4 | 50 | 120 | 15.5 | 7.9 | 43.0841 | yes | 7
12 | 2.8 | 50 | 140 | 19 | 7.7 | 33.1927 | yes | 7
13 | 2.9 | 50 | 145 | 20.6 | 7.7 | 30.1756 | yes | 7
14 | 2.8 | 50 | 140 | 21.5 | 7.6 | 27.0669 | yes | 7
15 | 2.7 | 50 | 135 | 21 | 7.6 | 27.6701 | yes | 7
16 | 2.8 | 50 | 140 | 14.5 | 7.7 | 44.748 | yes | 7
17 | 2.6 | 50 | 130 | 16.8 | 7.7 | 37.5594 | yes | 7
18 | 2.5 | 50 | 125 | 17.3 | 7.8 | 37.2727 | yes | 7
19 | 2.6 | 50 | 130 | 16.8 | 7.7 | 37.5594 | yes | 7
20 | 2.6 | 50 | 130 | 18.6 | 7.7 | 33.3222 | yes | 7
21 | 2.2 | 50 | 110 | 17 | 7.7 | 35.4187 | yes | 7
22 | 2 | 50 | 100 | 16 | 7.7 | 37.0032 | yes | 7
23 | 2 | 50 | 100 | 19 | 7.6 | 29.1995 | yes | 7
24 | 2.1 | 50 | 105 | 14.2 | 7.7 | 42.1719 | yes | 7
25 | 2 | 50 | 100 | 17.5 | 7.7 | 33.4899 | yes | 7
26 | 2.3 | 50 | 115 | 14.7 | 7.9 | 44.9169 | yes | 7
27 | 2.3 | 50 | 115 | 14.6 | 7.9 | 45.2151 | yes | 7
28 | 2.4 | 50 | 120 | 14.4 | 7.8 | 44.6661 | yes | 7
29 | 2.5 | 50 | 125 | 14.6 | 7.7 | 42.9702 | yes | 7
30 | 2.6 | 50 | 130 | 14.8 | 7.7 | 42.887 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2