## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-10-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.55 | 0.52 | 0.54 | 0.55 | 0.55
2 |  |  | 0.29 | 0.32 | 0.31 | 0.32 | 0.32
3 |  |  | 0.55 | 0.54 | 0.56 | 0.57 | 0.57
4 |  |  | 0.41 | 0.42 | 0.43 | 0.43 | 0.43
5 |  |  | 0.35 | 0.33 | 0.31 | 0.35 | 0.35
6 |  |  | 0.31 | 0.33 | 0.32 | 0.37 | 0.37
7 |  |  | 0.29 | 0.3 | 0.3 | 0.3 | 0.3
8 |  |  | 0.25 | 0.26 | 0.27 | 0.27 | 0.27
9 |  |  | 0.24 | 0.26 | 0.22 | 0.26 | 0.26
10 |  |  | .,22 | 0.21 | 0.24 | 0.26 | 0.26
11 |  |  | 0.24 | 0.25 | 0.24 | 0.28 | 0.28
12 |  |  | ..23 | 0.21 | 0.24 | 0.26 | 0.26
13 |  |  | 0.23 | 0.23 | 0.25 | 0.28 | 0.28
14 |  |  | 0.31 | 0.34 | 0.33 | 0.34 | 0.34
15 |  |  | 0.24 | 0.26 | 0.29 | 0.3 | 0.3
16 |  |  | 0.23 | 0.24 | 0.23 | 0.27 | 0.27
17 |  |  | 0.24 | 0.21 | 0.28 | 0.28 | 0.28
18 |  |  | 0.3 | 0.29 | 0.27 | 0.3 | 0.3
19 |  |  | 0.31 | 0.33 | 0.32 | 0.33 | 0.33
20 |  |  | 0.3 | 0.29 | 0.3 | 0.31 | 0.31
21 |  |  | 0.31 | 0.33 | 0.32 | 0.33 | 0.33
22 |  |  | 0.3 | 0.31 | 0.3 | 0.31 | 0.31
23 |  |  | 0.31 | 0.35 | 0.34 | 0.37 | 0.37
24 |  |  | 0.33 | 0.31 | 0.32 | 0.34 | 0.34
25 |  |  | 0.35 | 0.32 | 0.31 | 0.36 | 0.36
26 |  |  | 0.37 | 0.32 | 0.34 | 0.37 | 0.37
27 |  |  | 0.34 | 0.29 | 0.33 | 0.34 | 0.34
28 |  |  | 0.28 | 0.3 | 0.31 | 0.32 | 0.32
29 |  |  | 0.33 | 0.32 | 0.31 | 0.33 | 0.33
30 |  |  | 0.31 | 0.33 | 0.32 | 0.34 | 0.34
31 |  |  | 0.35 | 0.33 | 0.36 | 0.36 | 0.36
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:11/3/2021
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.6 | 50 | 130 | 15.4 | 7.7 | 41.2154 | yes | 7
2 | 2.2 | 50 | 110 | 16.7 | 7.6 | 34.8221 | yes | 7
3 | 2.1 | 50 | 105 | 15.4 | 7.7 | 38.9462 | yes | 7
4 | 2.1 | 50 | 105 | 16.4 | 7.6 | 35.1228 | yes | 7
5 | 2.1 | 50 | 105 | 13.4 | 7.7 | 44.4664 | yes | 7
6 | 3 | 50 | 150 | 14 | 7.6 | 45.6034 | yes | 7
7 | 2.7 | 50 | 135 | 9 | 7.7 | 64.2482 | yes | 7
8 | 2.7 | 50 | 135 | 12.1 | 7.7 | 52.0949 | yes | 7
9 | 2.8 | 50 | 140 | 12.5 | 7.7 | 51.0736 | yes | 7
10 | 2.1 | 50 | 105 | 9.7 | 7.8 | 59.237 | yes | 7
11 | 2.3 | 50 | 115 | 10.1 | 7.7 | 56.9169 | yes | 7
12 | 2.1 | 50 | 105 | 9.7 | 7.7 | 57.1386 | yes | 7
13 | 2.3 | 50 | 115 | 10.2 | 7.7 | 56.5337 | yes | 7
14 | 2.2 | 50 | 110 | 10.7 | 7.8 | 56.0082 | yes | 7
15 | 2.1 | 50 | 105 | 10.5 | 7.9 | 58.1749 | yes | 7
16 | 2.3 | 50 | 115 | 10.7 | 7.8 | 56.6594 | yes | 7
17 | 2.3 | 50 | 115 | 10.6 | 7.9 | 59.1381 | yes | 7
18 | 2.2 | 50 | 110 | 13 | 7.6 | 44.5117 | yes | 7
19 | 2.2 | 50 | 110 | 10.9 | 7.8 | 55.2579 | yes | 7
20 | 2.3 | 50 | 115 | 10.8 | 7.8 | 56.2781 | yes | 7
21 | 2.2 | 50 | 110 | 11 | 7.8 | 54.8868 | yes | 7
22 | 2.4 | 50 | 120 | 12.1 | 7.8 | 52.1619 | yes | 7
23 | 2.5 | 50 | 125 | 11.9 | 7.8 | 53.4784 | yes | 7
24 | 2.4 | 50 | 120 | 10.4 | 7.7 | 56.424 | yes | 7
25 | 2.4 | 50 | 120 | 11.3 | 7.7 | 53.1056 | yes | 7
26 | 2.5 | 50 | 125 | 11.6 | 7.8 | 54.5687 | yes | 7
27 | 2.4 | 50 | 120 | 11.9 | 7.8 | 52.8668 | yes | 7
28 | 2.4 | 50 | 120 | 11.9 | 7.8 | 52.8668 | yes | 7
29 | 2.3 | 50 | 115 | 10.6 | 7.8 | 57.0435 | yes | 7
30 | 2.3 | 50 | 115 | 10.2 | 7.9 | 60.7648 | yes | 7
31 | 2.2 | 50 | 110 | 9.8 | 8 | 63.9967 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2