## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-01-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.65 |  |  | 0.65
2 |  |  |  | 0.58 |  |  | 0.58
3 |  |  |  | 0.6 |  |  | 0.6
4 |  |  |  | 0.58 |  |  | 0.58
5 |  |  |  | 0.61 |  |  | 0.61
6 |  |  |  | 0.6 |  |  | 0.6
7 |  |  |  | 0.41 |  |  | 0.41
8 |  |  |  | 0.41 |  |  | 0.41
9 |  |  |  | 0.47 |  |  | 0.47
10 |  |  |  | 0.51 |  |  | 0.51
11 |  |  |  | 0.46 |  |  | 0.46
12 |  |  |  | 0.45 |  |  | 0.45
13 |  |  |  | 0.47 |  |  | 0.47
14 |  |  |  | 0.62 |  |  | 0.62
15 |  |  |  | 0.74 |  |  | 0.74
16 |  |  |  | 0.7 |  |  | 0.7
17 |  |  |  | 0.63 |  |  | 0.63
18 |  |  |  | 0.69 |  |  | 0.69
19 |  |  |  | 0.72 |  |  | 0.72
20 |  |  |  | 0.74 |  |  | 0.74
21 |  |  |  | 0.68 |  |  | 0.68
22 |  |  |  | 0.71 |  |  | 0.71
23 |  |  |  | 0.78 |  |  | 0.78
24 |  |  |  | 0.8 |  |  | 0.8
25 |  |  |  | 0.82 |  |  | 0.82
26 |  |  |  | 0.8 |  |  | 0.8
27 |  |  |  | 0.68 |  |  | 0.68
28 |  |  |  | 0.72 |  |  | 0.72
29 |  |  |  | 0.76 |  |  | 0.76
30 |  |  |  | 0.84 |  |  | 0.84
31 |  |  |  | 0.76 |  |  | 0.76
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-02-02
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.7 | 50 | 135 | 1.8 | 7.6 | 101.8708 | yes | 7
2 | 2.6 | 50 | 130 | 2.2 | 7.6 | 97.8833 | yes | 7
3 | 2.7 | 50 | 135 | 2.4 | 7.6 | 97.6868 | yes | 7
4 | 2.6 | 50 | 130 | 3.2 | 7.7 | 94.7438 | yes | 7
5 | 2.6 | 50 | 130 | 5.3 | 7.6 | 78.9182 | yes | 7
6 | 2.7 | 50 | 135 | 7.4 | 7.5 | 66.6348 | yes | 7
7 | 2.9 | 50 | 145 | 5.5 | 7.6 | 80.6481 | yes | 7
8 | 2.9 | 50 | 145 | 5 | 7.6 | 83.4885 | yes | 7
9 | 2.8 | 50 | 140 | 8.3 | 7.5 | 63.4021 | yes | 7
10 | 2.9 | 50 | 145 | 5.8 | 7.5 | 76.1407 | yes | 7
11 | 2.8 | 50 | 140 | 8.5 | 7.5 | 62.5446 | yes | 7
12 | 2.8 | 50 | 140 | 6 | 7.6 | 76.9942 | yes | 7
13 | 2.7 | 50 | 135 | 7.9 | 7.6 | 66.7848 | yes | 7
14 | 2.8 | 50 | 140 | 7.3 | 7.5 | 67.8826 | yes | 7
15 | 2.9 | 50 | 145 | 5.3 | 7.6 | 81.7718 | yes | 7
16 | 2.8 | 50 | 140 | 5.8 | 7.6 | 78.0643 | yes | 7
17 | 2.8 | 50 | 140 | 5.6 | 7.6 | 79.15 | yes | 7
18 | 2.4 | 50 | 120 | 5.6 | 7.6 | 75.4965 | yes | 7
19 | 2.2 | 50 | 110 | 6 | 7.6 | 71.7371 | yes | 7
20 | 2.3 | 50 | 115 | 7.1 | 7.6 | 67.3124 | yes | 7
21 | 2.3 | 50 | 115 | 6.6 | 7.6 | 69.6571 | yes | 7
22 | 2.1 | 50 | 105 | 6.1 | 7.7 | 73.0387 | yes | 7
23 | 2.1 | 50 | 105 | 5.2 | 7.8 | 80.6251 | yes | 7
24 | 2.1 | 50 | 105 | 3.3 | 7.8 | 91.99 | yes | 7
25 | 2.2 | 50 | 110 | 5.1 | 7.7 | 79.18 | yes | 7
26 | 2.1 | 50 | 105 | 3.1 | 7.8 | 93.2805 | yes | 7
27 | 2.5 | 50 | 125 | 5.8 | 7.7 | 78.1677 | yes | 7
28 | 2.7 | 50 | 135 | 1.2 | 7.8 | 114.495 | yes | 7
29 | 2.6 | 50 | 130 | 2.2 | 7.8 | 105.4598 | yes | 7
30 | 2.6 | 50 | 130 | 4.1 | 7.8 | 92.3505 | yes | 7
31 | 2.6 | 50 | 130 | 5.3 | 7.8 | 84.9602 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2