## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-02-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.78 |  |  | 0.78
2 |  |  |  | 0.84 |  |  | 0.84
3 |  |  |  | 0.88 |  |  | 0.88
4 |  |  |  | 0.86 |  |  | 0.86
5 |  |  |  | 0.88 |  |  | 0.88
6 |  |  |  | 0.82 |  |  | 0.82
7 |  |  |  | 0.62 |  |  | 0.62
8 |  |  |  | 0.6 |  |  | 0.6
9 |  |  |  | 0.79 |  |  | 0.79
10 |  |  |  | 0.69 |  |  | 0.69
11 |  |  |  | 0.7 |  |  | 0.7
12 |  |  |  | 0.71 |  |  | 0.71
13 |  |  |  | 0.55 |  |  | 0.55
14 |  |  |  | 0.53 |  |  | 0.53
15 |  |  |  | 0.46 |  |  | 0.46
16 |  |  |  | 0.46 |  |  | 0.46
17 |  |  |  | 0.47 |  |  | 0.47
18 |  |  |  | 0.44 |  |  | 0.44
19 |  |  |  | 0.46 |  |  | 0.46
20 |  |  |  | 0.42 |  |  | 0.42
21 |  |  |  | 0.38 |  |  | 0.38
22 |  |  |  | 0.37 |  |  | 0.37
23 |  |  |  | 0.47 |  |  | 0.47
24 |  |  |  | 0.34 |  |  | 0.34
25 |  |  |  | 0.36 |  |  | 0.36
26 |  |  |  | 0.37 |  |  | 0.37
27 |  |  |  | 0.34 |  |  | 0.34
28 |  |  |  | 0.5 |  |  | 0.5
29 | [6 empty] | 0
30 | [6 empty] | 0
31 | [6 empty] | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-02-28
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.1 | 50 | 105 | 5.6 | 7.8 | 78.4269 | yes | 7
2 | 2.3 | 50 | 115 | 3.7 | 7.8 | 91.6222 | yes | 7
3 | 2.1 | 50 | 105 | 4.8 | 7.8 | 82.8885 | yes | 7
4 | 2 | 50 | 100 | 4.4 | 7.8 | 84.213 | yes | 7
5 | 2.2 | 50 | 110 | 4.9 | 7.8 | 83.2986 | yes | 7
6 | 2.1 | 50 | 105 | 8.5 | 7.8 | 64.2722 | yes | 7
7 | 2.2 | 50 | 110 | 8 | 7.7 | 64.8816 | yes | 7
8 | 2.1 | 50 | 105 | 8.5 | 7.7 | 61.9817 | yes | 7
9 | 2.2 | 50 | 110 | 9.2 | 7.7 | 59.7953 | yes | 7
10 | 2.1 | 50 | 105 | 8.6 | 7.7 | 61.5617 | yes | 7
11 | 2.9 | 50 | 145 | 4.6 | 7.9 | 95.9372 | yes | 7
12 | 2.8 | 50 | 140 | 5.4 | 7.8 | 86.4018 | yes | 7
13 | 2.4 | 50 | 120 | 5.1 | 7.9 | 87.2939 | yes | 7
14 | 2.5 | 50 | 125 | 8.5 | 7.9 | 69.8537 | yes | 7
15 | 2.2 | 50 | 110 | 6.6 | 7.9 | 76.8416 | yes | 7
16 | 2.2 | 50 | 110 | 7 | 7.9 | 74.7522 | yes | 7
17 | 2.3 | 50 | 115 | 7.2 | 7.9 | 74.6043 | yes | 7
18 | 2.1 | 50 | 105 | 4.7 | 7.9 | 86.6074 | yes | 7
19 | 2.1 | 50 | 105 | 4.9 | 7.9 | 85.4136 | yes | 7
20 | 2.5 | 50 | 125 | 5.6 | 7.9 | 85.3243 | yes | 7
21 | 2.8 | 50 | 140 | 6.6 | 7.9 | 82.4963 | yes | 7
22 | 2.9 | 50 | 145 | 4.3 | 8 | 101.6855 | yes | 7
23 | 2.9 | 50 | 145 | 3.3 | 8 | 109.0653 | yes | 7
24 | 2.4 | 50 | 120 | 4.1 | 7.9 | 93.5838 | yes | 7
25 | 2.4 | 50 | 120 | 4.3 | 7.9 | 92.2888 | yes | 7
26 | 2.2 | 50 | 110 | 5.4 | 7.9 | 83.4885 | yes | 7
27 | 2 | 50 | 100 | 5.9 | 7.9 | 78.7615 | yes | 7
28 | 2 | 50 | 100 | 7.5 | 7.8 | 68.0164 | yes | 7
29 |  | 50 | 0 |  |  | 8.3699 | yes | 7
30 |  | 50 | 0 |  |  | 8.3699 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2