## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-03-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.42 |  |  | 0.42
2 |  |  |  | 0.5 |  |  | 0.5
3 |  |  |  | 0.5 |  |  | 0.5
4 |  |  |  | 0.51 |  |  | 0.51
5 |  |  |  | 0.48 |  |  | 0.48
6 |  |  |  | 0.68 |  |  | 0.68
7 |  |  |  | 0.81 |  |  | 0.81
8 |  |  |  | 0.94 |  |  | 0.94
9 |  |  |  | 0.81 |  |  | 0.81
10 |  |  |  | 0.66 |  |  | 0.66
11 |  |  |  | 0.64 |  |  | 0.64
12 |  |  |  | 0.71 |  |  | 0.71
13 |  |  |  | 0.67 |  |  | 0.67
14 |  |  |  | 0.56 |  |  | 0.56
15 |  |  |  | 0.58 |  |  | 0.58
16 |  |  |  | 0.58 |  |  | 0.58
17 |  |  |  | 0.67 |  |  | 0.67
18 |  |  |  | 0.68 |  |  | 0.68
19 |  |  |  | 0.58 |  |  | 0.58
20 |  |  |  | 0.54 |  |  | 0.54
21 |  |  |  | 0.52 |  |  | 0.52
22 |  |  |  | 0.63 |  |  | 0.63
23 |  |  |  | 0.52 |  |  | 0.52
24 |  |  |  | 0.47 |  |  | 0.47
25 |  |  |  | 0.4 |  |  | 0.4
26 |  |  |  | 0.41 |  |  | 0.41
27 |  |  |  | 0.36 |  |  | 0.36
28 |  |  |  | 0.38 |  |  | 0.38
29 |  |  |  | 0.45 |  |  | 0.45
30 |  |  |  | 0.41 |  |  | 0.41
31 |  |  |  | 0.46 |  |  | 0.46
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-04-02
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.1 | 50 | 105 | 8.3 | 7.8 | 65.1551 | yes | 7
2 | 2.2 | 50 | 110 | 7.4 | 7.9 | 72.723 | yes | 7
3 | 2 | 50 | 100 | 6.4 | 7.9 | 76.0904 | yes | 7
4 | 2.1 | 50 | 105 | 7.8 | 7.9 | 69.9259 | yes | 7
5 | 2.2 | 50 | 110 | 8.5 | 7.9 | 67.4387 | yes | 7
6 | 2.4 | 50 | 120 | 8.2 | 7.9 | 70.4734 | yes | 7
7 | 2.4 | 50 | 120 | 7.6 | 7.9 | 73.4389 | yes | 7
8 | 2.2 | 50 | 110 | 6.6 | 7.8 | 74.0715 | yes | 7
9 | 2.1 | 50 | 105 | 6.5 | 7.8 | 73.7094 | yes | 7
10 | 2.1 | 50 | 105 | 4.6 | 7.8 | 84.0452 | yes | 7
11 | 2 | 50 | 100 | 5.4 | 7.8 | 78.5828 | yes | 7
12 | 2.1 | 50 | 105 | 9.5 | 7.7 | 57.9166 | yes | 7
13 | 2.1 | 50 | 105 | 9.1 | 7.7 | 59.5072 | yes | 7
14 | 2.2 | 50 | 110 | 7.4 | 7.7 | 67.5969 | yes | 7
15 | 2.3 | 50 | 115 | 6 | 7.9 | 81.0464 | yes | 7
16 | 2.4 | 50 | 120 | 6.5 | 7.9 | 79.225 | yes | 7
17 | 2.8 | 50 | 140 | 7.4 | 7.8 | 75.2405 | yes | 7
18 | 2.8 | 50 | 140 | 9.5 | 7.8 | 65.1491 | yes | 7
19 | 2.8 | 50 | 140 | 7.7 | 7.8 | 73.7024 | yes | 7
20 | 2.1 | 50 | 105 | 8.2 | 7.9 | 68.0355 | yes | 7
21 | 2.3 | 50 | 115 | 8.6 | 7.8 | 65.3443 | yes | 7
22 | 2 | 50 | 100 | 10 | 7.7 | 55.3498 | yes | 7
23 | 2.4 | 50 | 120 | 12.6 | 7.7 | 48.4985 | yes | 7
24 | 2.3 | 50 | 115 | 13.4 | 7.7 | 45.4829 | yes | 7
25 | 2.3 | 50 | 115 | 8.3 | 7.8 | 66.6973 | yes | 7
26 | 2.1 | 50 | 105 | 9.4 | 7.7 | 58.3099 | yes | 7
27 | 2.1 | 50 | 105 | 11.6 | 7.7 | 50.2874 | yes | 7
28 | 2 | 50 | 100 | 12.3 | 7.8 | 49.1639 | yes | 7
29 | 2.1 | 50 | 105 | 9.2 | 7.8 | 61.2815 | yes | 7
30 | 2.1 | 50 | 105 | 9.3 | 7.8 | 60.8666 | yes | 7
31 | 2.1 | 50 | 105 | 11.4 | 7.8 | 52.8182 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2