## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-04-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.37 |  |  | 0.37
2 |  |  |  | 0.34 |  |  | 0.34
3 |  |  |  | 0.38 |  |  | 0.38
4 |  |  |  | 0.43 |  |  | 0.43
5 |  |  |  | 0.33 |  |  | 0.33
6 |  |  |  | 0.5 |  |  | 0.5
7 |  |  |  | 0.73 |  |  | 0.73
8 |  |  |  | 0.72 |  |  | 0.72
9 |  |  |  | 0.75 |  |  | 0.75
10 |  |  |  | 0.72 |  |  | 0.72
11 |  |  |  | 0.71 |  |  | 0.71
12 |  |  |  | 0.64 |  |  | 0.64
13 |  |  |  | 0.6 |  |  | 0.6
14 |  |  |  | 0.7 |  |  | 0.7
15 |  |  |  | 0.71 |  |  | 0.71
16 |  |  |  | 0.68 |  |  | 0.68
17 |  |  |  | 0.64 |  |  | 0.64
18 |  |  |  | 0.62 |  |  | 0.62
19 |  |  |  | 0.47 |  |  | 0.47
20 |  |  |  | 0.41 |  |  | 0.41
21 |  |  |  | 0.43 |  |  | 0.43
22 |  |  |  | 0.41 |  |  | 0.41
23 |  |  |  | 0.4 |  |  | 0.4
24 |  |  |  | 0.42 |  |  | 0.42
25 |  |  |  | 0.44 |  |  | 0.44
26 |  |  |  | 0.48 |  |  | 0.48
27 |  |  |  | 0.39 |  |  | 0.39
28 |  |  |  | 0.38 |  |  | 0.38
29 |  |  |  | 0.42 |  |  | 0.42
30 |  |  |  | 0.44 |  |  | 0.44
31 | [6 empty] | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-05-02
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 50 | 110 | 8.5 | 7.8 | 65.0274 | yes | 7
2 | 2.1 | 50 | 105 | 8.6 | 7.8 | 63.8356 | yes | 7
3 | 2.5 | 50 | 125 | 9.2 | 7.8 | 64.2062 | yes | 7
4 | 2.4 | 50 | 120 | 8.7 | 7.8 | 65.6629 | yes | 7
5 | 2.2 | 50 | 110 | 8.9 | 7.8 | 63.278 | yes | 7
6 | 2.1 | 50 | 105 | 12.4 | 7.7 | 47.6752 | yes | 7
7 | 2.2 | 50 | 110 | 7.4 | 7.8 | 70.1101 | yes | 7
8 | 2.7 | 50 | 135 | 8.8 | 7.8 | 67.5462 | yes | 7
9 | 2.5 | 50 | 125 | 8.3 | 7.9 | 70.8187 | yes | 7
10 | 2.3 | 50 | 115 | 8.8 | 7.9 | 66.8474 | yes | 7
11 | 2.1 | 50 | 105 | 6.6 | 7.9 | 75.9397 | yes | 7
12 | 2.1 | 50 | 105 | 7.8 | 7.8 | 67.4197 | yes | 7
13 | 2 | 50 | 100 | 7.3 | 7.8 | 68.9544 | yes | 7
14 | 2 | 50 | 100 | 6.7 | 7.7 | 69.2723 | yes | 7
15 | 2.1 | 50 | 105 | 6.8 | 7.7 | 69.6113 | yes | 7
16 | 2.6 | 50 | 130 | 8.1 | 7.7 | 67.5272 | yes | 7
17 | 2.4 | 50 | 120 | 8.6 | 7.7 | 63.7522 | yes | 7
18 | 2.3 | 50 | 115 | 10.6 | 7.7 | 55.0288 | yes | 7
19 | 2.8 | 50 | 140 | 6.8 | 7.8 | 78.4195 | yes | 7
20 | 2.5 | 50 | 125 | 7.2 | 7.7 | 70.9853 | yes | 7
21 | 2.3 | 50 | 115 | 7.6 | 7.8 | 69.9719 | yes | 7
22 | 2.1 | 50 | 105 | 7.3 | 7.8 | 69.7684 | yes | 7
23 | 2 | 50 | 100 | 14.7 | 7.6 | 38.8787 | yes | 7
24 | 2.1 | 50 | 105 | 13.8 | 7.7 | 43.3042 | yes | 7
25 | 2 | 50 | 100 | 10.6 | 7.8 | 55.0999 | yes | 7
26 | 2.1 | 50 | 105 | 9.1 | 7.8 | 61.6995 | yes | 7
27 | 2 | 50 | 100 | 8.4 | 7.8 | 63.9609 | yes | 7
28 | 2.1 | 50 | 105 | 8.6 | 7.8 | 63.8356 | yes | 7
29 | 2.1 | 50 | 105 | 10.4 | 7.8 | 56.4972 | yes | 7
30 | 2.1 | 50 | 105 | 9.2 | 7.8 | 61.2815 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2