## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-05-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.33 |  |  | 0.33
2 |  |  |  | 0.29 |  |  | 0.29
3 |  |  |  | 0.34 |  |  | 0.34
4 |  |  |  | 0.36 |  |  | 0.36
5 |  |  |  | 0.29 |  |  | 0.29
6 |  |  |  | 0.29 |  |  | 0.29
7 |  |  |  | 0.35 |  |  | 0.35
8 |  |  |  | 0.31 |  |  | 0.31
9 |  |  |  | 0.27 |  |  | 0.27
10 |  |  |  | 0.4 |  |  | 0.4
11 |  |  |  | 0.32 |  |  | 0.32
12 |  |  |  | 0.36 |  |  | 0.36
13 |  |  |  | 0.34 |  |  | 0.34
14 |  |  |  | 0.38 |  |  | 0.38
15 |  |  |  | 0.36 |  |  | 0.36
16 |  |  |  | 0.38 |  |  | 0.38
17 |  |  |  | 0.36 |  |  | 0.36
18 |  |  |  | 0.53 |  |  | 0.53
19 |  |  |  | 0.41 |  |  | 0.41
20 |  |  |  | 0.36 |  |  | 0.36
21 |  |  |  | 0.29 |  |  | 0.29
22 |  |  |  | 0.3 |  |  | 0.3
23 |  |  |  | 0.32 |  |  | 0.32
24 |  |  |  | 0.36 |  |  | 0.36
25 |  |  |  | 0.34 |  |  | 0.34
26 |  |  |  | 0.37 |  |  | 0.37
27 |  |  |  | 0.37 |  |  | 0.37
28 |  |  |  | 0.34 |  |  | 0.34
29 |  |  |  | 0.3 |  |  | 0.3
30 |  |  |  | 0.26 |  |  | 0.26
31 |  |  |  | 0.24 |  |  | 0.24
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-06-02
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 50 | 110 | 13.9 | 7.7 | 43.5076 | yes | 7
2 | 2.2 | 50 | 110 | 9.6 | 7.8 | 60.3368 | yes | 7
3 | 2.3 | 50 | 115 | 13.4 | 7.7 | 45.4829 | yes | 7
4 | 2.4 | 50 | 120 | 15.5 | 7.7 | 40.0263 | yes | 7
5 | 2.7 | 50 | 135 | 11 | 7.8 | 58.1533 | yes | 7
6 | 2.6 | 50 | 130 | 10.1 | 7.8 | 61.0993 | yes | 7
7 | 2.8 | 50 | 140 | 9.8 | 7.8 | 63.8296 | yes | 7
8 | 2.5 | 50 | 125 | 10.2 | 7.8 | 59.9845 | yes | 7
9 | 2.1 | 50 | 105 | 9.3 | 7.8 | 60.8666 | yes | 7
10 | 2.1 | 50 | 105 | 11.4 | 7.7 | 50.9647 | yes | 7
11 | 2.4 | 50 | 120 | 12.6 | 7.7 | 48.4985 | yes | 7
12 | 2.6 | 50 | 130 | 10.8 | 7.7 | 56.2053 | yes | 7
13 | 2.8 | 50 | 140 | 6.1 | 7.8 | 82.3087 | yes | 7
14 | 2.8 | 50 | 140 | 10.2 | 7.7 | 59.9065 | yes | 7
15 | 2.5 | 50 | 125 | 11.8 | 7.7 | 51.9468 | yes | 7
16 | 2.3 | 50 | 115 | 12.8 | 7.8 | 49.0938 | yes | 7
17 | 2.4 | 50 | 120 | 13.2 | 7.7 | 46.6122 | yes | 7
18 | 2.3 | 50 | 115 | 12.8 | 7.7 | 47.3242 | yes | 7
19 | 2.5 | 50 | 125 | 12.1 | 7.7 | 50.9133 | yes | 7
20 | 2.6 | 50 | 130 | 14.2 | 7.7 | 44.6251 | yes | 7
21 | 2.6 | 50 | 130 | 14.8 | 7.7 | 42.887 | yes | 7
22 | 2.5 | 50 | 125 | 16.6 | 7.6 | 36.2692 | yes | 7
23 | 2.4 | 50 | 120 | 13.8 | 7.7 | 44.7981 | yes | 7
24 | 2.6 | 50 | 130 | 13.2 | 7.7 | 47.6769 | yes | 7
25 | 2.8 | 50 | 140 | 12.8 | 7.7 | 50.0716 | yes | 7
26 | 2.9 | 50 | 145 | 13.6 | 7.8 | 49.8279 | yes | 7
27 | 3 | 50 | 150 | 12.5 | 7.8 | 54.1887 | yes | 7
28 | 2.9 | 50 | 145 | 13.1 | 7.9 | 53.424 | yes | 7
29 | 2.7 | 50 | 135 | 14.6 | 7.7 | 43.9531 | yes | 7
30 | 2.6 | 50 | 130 | 13.9 | 7.7 | 45.5199 | yes | 7
31 | 2.5 | 50 | 125 | 16.3 | 7.7 | 38.3895 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2