## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-07-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.32 |  |  | 0.32
2 |  |  |  | 0.3 |  |  | 0.3
3 |  |  |  | 0.26 |  |  | 0.26
4 |  |  |  | 0.28 |  |  | 0.28
5 |  |  |  | 0.24 |  |  | 0.24
6 |  |  |  | 0.22 |  |  | 0.22
7 |  |  |  | 0.24 |  |  | 0.24
8 |  |  |  | 0.24 |  |  | 0.24
9 |  |  |  | 0.34 |  |  | 0.34
10 |  |  |  | 0.46 |  |  | 0.46
11 |  |  |  | 0.28 |  |  | 0.28
12 |  |  |  | 0.34 |  |  | 0.34
13 |  |  |  | 0.24 |  |  | 0.24
14 |  |  |  | 0.32 |  |  | 0.32
15 |  |  |  | 0.37 |  |  | 0.37
16 |  |  |  | 0.38 |  |  | 0.38
17 |  |  |  | 0.42 |  |  | 0.42
18 |  |  |  | 0.4 |  |  | 0.4
19 |  |  |  | 0.38 |  |  | 0.38
20 |  |  |  | 0.34 |  |  | 0.34
21 |  |  |  | 0.33 |  |  | 0.33
22 |  |  |  | 0.36 |  |  | 0.36
23 |  |  |  | 0.32 |  |  | 0.32
24 |  |  |  | 0.34 |  |  | 0.34
25 |  |  |  | 0.47 |  |  | 0.47
26 |  |  |  | 0.44 |  |  | 0.44
27 |  |  |  | 0.36 |  |  | 0.36
28 |  |  |  | 0.28 |  |  | 0.28
29 |  |  |  | 0.23 |  |  | 0.23
30 |  |  |  | 0.23 |  |  | 0.23
31 |  |  |  | 0.49 |  |  | 0.49
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-08-02
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.5 | 50 | 125 | 20.2 | 7.7 | 29.6105 | yes | 7
2 | 2.4 | 50 | 120 | 18.2 | 7.8 | 34.7118 | yes | 7
3 | 2.4 | 50 | 120 | 17.8 | 7.8 | 35.6477 | yes | 7
4 | 2.3 | 50 | 115 | 18.3 | 7.7 | 32.8543 | yes | 7
5 | 2.1 | 50 | 105 | 17.2 | 7.8 | 35.8561 | yes | 7
6 | 2 | 50 | 100 | 18.6 | 7.9 | 33.5139 | yes | 7
7 | 2.2 | 50 | 110 | 21.2 | 7.9 | 28.8267 | yes | 7
8 | 2.1 | 50 | 105 | 20.8 | 7.9 | 29.2717 | yes | 7
9 | 2 | 50 | 100 | 20.3 | 7.9 | 29.9225 | yes | 7
10 | 2 | 50 | 100 | 20.4 | 7.7 | 27.5961 | yes | 7
11 | 2.5 | 50 | 125 | 19.8 | 7.7 | 30.412 | yes | 7
12 | 2.3 | 50 | 115 | 21.6 | 7.8 | 27.3528 | yes | 7
13 | 2.1 | 50 | 105 | 18.5 | 7.8 | 32.8846 | yes | 7
14 | 2.4 | 50 | 120 | 18.8 | 7.8 | 33.3529 | yes | 7
15 | 2.3 | 50 | 115 | 17.4 | 7.8 | 36.1951 | yes | 7
16 | 2.2 | 50 | 110 | 18.8 | 7.8 | 32.6027 | yes | 7
17 | 2.1 | 50 | 105 | 19.5 | 7.8 | 30.7637 | yes | 7
18 | 2.4 | 50 | 120 | 19.1 | 7.7 | 31.505 | yes | 7
19 | 2.4 | 50 | 120 | 18.6 | 7.7 | 32.5727 | yes | 7
20 | 2.9 | 50 | 145 | 20.9 | 7.9 | 31.8527 | yes | 7
21 | 2.8 | 50 | 140 | 17.8 | 7.9 | 38.7044 | yes | 7
22 | 2.7 | 50 | 135 | 18.5 | 7.9 | 36.5297 | yes | 7
23 | 2.6 | 50 | 130 | 17.6 | 7.9 | 38.3425 | yes | 7
24 | 2.5 | 50 | 125 | 21.2 | 7.9 | 29.8304 | yes | 7
25 | 2.1 | 50 | 105 | 16.8 | 7.9 | 38.2057 | yes | 7
26 | 2.2 | 50 | 110 | 27.2 | 7.8 | 18.5421 | yes | 7
27 | 2.2 | 50 | 110 | 26.4 | 7.9 | 20.325 | yes | 7
28 | 2.2 | 50 | 110 | 23.6 | 7.9 | 24.545 | yes | 7
29 | 2.1 | 50 | 105 | 21.1 | 7.9 | 28.6906 | yes | 7
30 | 2 | 50 | 100 | 21.9 | 7.9 | 26.8863 | yes | 7
31 | 2.1 | 50 | 105 | 26.5 | 7.9 | 19.9561 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2