## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-08-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.45 |  |  | 0.45
2 |  |  |  | 0.29 |  |  | 0.29
3 |  |  |  | 0.23 |  |  | 0.23
4 |  |  |  | 0.34 |  |  | 0.34
5 |  |  |  | 0.31 |  |  | 0.31
6 |  |  |  | 0.28 |  |  | 0.28
7 |  |  |  | 0.29 |  |  | 0.29
8 |  |  |  | 0.31 |  |  | 0.31
9 |  |  |  | 0.29 |  |  | 0.29
10 |  |  |  | 0.27 |  |  | 0.27
11 |  |  |  | 0.28 |  |  | 0.28
12 |  |  |  | 0.26 |  |  | 0.26
13 |  |  |  | 0.28 |  |  | 0.28
14 |  |  |  | 0.24 |  |  | 0.24
15 |  |  |  | 0.26 |  |  | 0.26
16 |  |  |  | 0.34 |  |  | 0.34
17 |  |  |  | 0.31 |  |  | 0.31
18 |  |  |  | 0.3 |  |  | 0.3
19 |  |  |  | 0.35 |  |  | 0.35
20 |  |  |  | 0.34 |  |  | 0.34
21 |  |  |  | 0.29 |  |  | 0.29
22 |  |  |  | 0.37 |  |  | 0.37
23 |  |  |  | 0.22 |  |  | 0.22
24 |  |  |  | 0.24 |  |  | 0.24
25 |  |  |  | 0.34 |  |  | 0.34
26 |  |  |  | 0.29 |  |  | 0.29
27 |  |  |  | 0.25 |  |  | 0.25
28 |  |  |  | 0.3 |  |  | 0.3
29 |  |  |  | 0.32 |  |  | 0.32
30 |  |  |  | 0.28 |  |  | 0.28
31 |  |  |  | 0.34 |  |  | 0.34
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-09-01
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 50 | 100 | 27.3 | 7.9 | 18.6859 | yes | 7
2 | 2.2 | 50 | 110 | 20.7 | 7.9 | 29.8059 | yes | 7
3 | 2.5 | 50 | 125 | 25.3 | 7.9 | 22.6608 | yes | 7
4 | 2.6 | 50 | 130 | 19.1 | 7.9 | 34.7047 | yes | 7
5 | 2.5 | 50 | 125 | 23.8 | 7.8 | 24.1475 | yes | 7
6 | 2.5 | 50 | 125 | 22.6 | 7.9 | 27.1647 | yes | 7
7 | 2.4 | 50 | 120 | 19.6 | 7.9 | 32.8139 | yes | 7
8 | 2.4 | 50 | 120 | 21.4 | 7.9 | 29.1007 | yes | 7
9 | 2.2 | 50 | 110 | 20.3 | 7.9 | 30.6125 | yes | 7
10 | 2.2 | 50 | 110 | 21.9 | 7.9 | 27.5082 | yes | 7
11 | 2.3 | 50 | 115 | 22.9 | 7.9 | 26.0219 | yes | 7
12 | 2.4 | 50 | 120 | 23.2 | 7.9 | 25.7974 | yes | 7
13 | 2.3 | 50 | 115 | 21.6 | 7.9 | 28.3883 | yes | 7
14 | 2.2 | 50 | 110 | 24.6 | 8 | 23.8226 | yes | 7
15 | 2.3 | 50 | 115 | 23.6 | 7.9 | 24.8281 | yes | 7
16 | 2.3 | 50 | 115 | 18.6 | 8 | 35.981 | yes | 7
17 | 2.4 | 50 | 120 | 21.6 | 8 | 29.7998 | yes | 7
18 | 2.4 | 50 | 120 | 22.3 | 8 | 28.438 | yes | 7
19 | 2.3 | 50 | 115 | 21.5 | 8 | 29.6593 | yes | 7
20 | 2.3 | 50 | 115 | 22.2 | 8 | 28.3037 | yes | 7
21 | 2.3 | 50 | 115 | 18.3 | 8 | 36.7056 | yes | 7
22 | 2.8 | 50 | 140 | 24.4 | 7.7 | 23.1255 | yes | 7
23 | 2.5 | 50 | 125 | 21.9 | 7.8 | 27.429 | yes | 7
24 | 2.7 | 50 | 135 | 19.9 | 7.8 | 32.0723 | yes | 7
25 | 2.6 | 50 | 130 | 20.4 | 7.8 | 30.6691 | yes | 7
26 | 2.7 | 50 | 135 | 22.4 | 7.8 | 27.1395 | yes | 7
27 | 2.5 | 50 | 125 | 23.8 | 7.8 | 24.1475 | yes | 7
28 | 2.4 | 50 | 120 | 22.1 | 7.9 | 27.7699 | yes | 7
29 | 2.3 | 50 | 115 | 21.6 | 7.9 | 28.3883 | yes | 7
30 | 2.5 | 50 | 125 | 19.8 | 7.9 | 32.7501 | yes | 7
31 | 2.4 | 50 | 120 | 21.6 | 7.9 | 28.7143 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2