## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-09-30
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.36 |  |  | 0.36
2 |  |  |  | 0.29 |  |  | 0.29
3 |  |  |  | 0.24 |  |  | 0.24
4 |  |  |  | 0.23 |  |  | 0.23
5 |  |  |  | 0.19 |  |  | 0.19
6 |  |  |  | 0.2 |  |  | 0.2
7 |  |  |  | 0.19 |  |  | 0.19
8 |  |  |  | 0.26 |  |  | 0.26
9 |  |  |  | 0.22 |  |  | 0.22
10 |  |  |  | 0.21 |  |  | 0.21
11 |  |  |  | 0.24 |  |  | 0.24
12 |  |  |  | 0.26 |  |  | 0.26
13 |  |  |  | 0.27 |  |  | 0.27
14 |  |  |  | 0.24 |  |  | 0.24
15 |  |  |  | 0.22 |  |  | 0.22
16 |  |  |  | 0.26 |  |  | 0.26
17 |  |  |  | 0.24 |  |  | 0.24
18 |  |  |  | 0.25 |  |  | 0.25
19 |  |  |  | 0.23 |  |  | 0.23
20 |  |  |  | 0.28 |  |  | 0.28
21 |  |  |  | 0.27 |  |  | 0.27
22 |  |  |  | 0.34 |  |  | 0.34
23 |  |  |  | 0.41 |  |  | 0.41
24 |  |  |  | 0.38 |  |  | 0.38
25 |  |  |  | 0.36 |  |  | 0.36
26 |  |  |  | 0.32 |  |  | 0.32
27 |  |  |  | 0.27 |  |  | 0.27
28 |  |  |  | 0.49 |  |  | 0.49
29 |  |  |  | 0.37 |  |  | 0.37
30 |  |  |  | 0.28 |  |  | 0.28
31 | [6 empty] | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-10-03
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.3 | 50 | 115 | 19.1 | 8 | 34.8043 | yes | 7
2 | 2.3 | 50 | 115 | 25.7 | 7.8 | 20.7628 | yes | 7
3 | 2.5 | 50 | 125 | 20.4 | 7.8 | 30.3216 | yes | 7
4 | 2.5 | 50 | 125 | 24.8 | 7.7 | 21.747 | yes | 7
5 | 2.5 | 50 | 125 | 17.1 | 7.8 | 37.7711 | yes | 7
6 | 2.6 | 50 | 130 | 23.8 | 7.7 | 23.5311 | yes | 7
7 | 2.7 | 50 | 135 | 18 | 7.8 | 36.3955 | yes | 7
8 | 2.9 | 50 | 145 | 15.7 | 7.8 | 43.366 | yes | 7
9 | 2.6 | 50 | 130 | 18.2 | 7.8 | 35.5094 | yes | 7
10 | 2.4 | 50 | 120 | 16.3 | 7.9 | 40.8597 | yes | 7
11 | 2.4 | 50 | 120 | 18.4 | 7.9 | 35.5421 | yes | 7
12 | 2.3 | 50 | 115 | 20.1 | 7.9 | 31.3791 | yes | 7
13 | 2.3 | 50 | 115 | 19.1 | 7.9 | 33.5414 | yes | 7
14 | 2.4 | 50 | 120 | 18.6 | 7.8 | 33.8 | yes | 7
15 | 2.5 | 50 | 125 | 18.8 | 7.8 | 33.7343 | yes | 7
16 | 2.5 | 50 | 125 | 19.5 | 7.9 | 33.411 | yes | 7
17 | 2.6 | 50 | 130 | 18.2 | 7.9 | 36.8447 | yes | 7
18 | 2.4 | 50 | 120 | 19.5 | 7.9 | 33.0332 | yes | 7
19 | 2.4 | 50 | 120 | 17.7 | 7.8 | 35.8855 | yes | 7
20 | 2.3 | 50 | 115 | 16.6 | 7.8 | 38.1706 | yes | 7
21 | 2.2 | 50 | 110 | 15.9 | 7.9 | 41.0183 | yes | 7
22 | 2.4 | 50 | 120 | 15.6 | 7.9 | 42.7997 | yes | 7
23 | 2.5 | 50 | 125 | 14.1 | 7.9 | 47.8032 | yes | 7
24 | 2.4 | 50 | 120 | 16.3 | 7.8 | 39.382 | yes | 7
25 | 2.5 | 50 | 125 | 19.2 | 7.8 | 32.8476 | yes | 7
26 | 2.5 | 50 | 125 | 22.5 | 7.8 | 26.3486 | yes | 7
27 | 2.6 | 50 | 130 | 20.5 | 7.8 | 30.4651 | yes | 7
28 | 2.9 | 50 | 145 | 17.6 | 7.8 | 38.233 | yes | 7
29 | 2.9 | 50 | 145 | 16.2 | 7.8 | 41.9532 | yes | 7
30 | 2.9 | 50 | 145 | 16 | 7.8 | 42.5128 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2