## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-10-31
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.27 |  |  | 0.27
2 |  |  |  | 0.38 |  |  | 0.38
3 |  |  |  | 0.33 |  |  | 0.33
4 |  |  |  | 0.25 |  |  | 0.25
5 |  |  |  | 0.26 |  |  | 0.26
6 |  |  |  | 0.27 |  |  | 0.27
7 |  |  |  | 0.24 |  |  | 0.24
8 |  |  |  | 0.26 |  |  | 0.26
9 |  |  |  | 0.28 |  |  | 0.28
10 |  |  |  | 0.32 |  |  | 0.32
11 |  |  |  | 0.28 |  |  | 0.28
12 |  |  |  | 0.31 |  |  | 0.31
13 |  |  |  | 0.23 |  |  | 0.23
14 |  |  |  | 0.31 |  |  | 0.31
15 |  |  |  | 0.31 |  |  | 0.31
16 |  |  |  | 0.28 |  |  | 0.28
17 |  |  |  | 0.26 |  |  | 0.26
18 |  |  |  | 0.33 |  |  | 0.33
19 |  |  |  | 0.35 |  |  | 0.35
20 |  |  |  | 0.34 |  |  | 0.34
21 |  |  |  | 0.31 |  |  | 0.31
22 |  |  |  | 0.36 |  |  | 0.36
23 |  |  |  | 0.28 |  |  | 0.28
24 |  |  |  | 0.3 |  |  | 0.3
25 |  |  |  | 0.32 |  |  | 0.32
26 |  |  |  | 0.26 |  |  | 0.26
27 |  |  |  | 0.27 |  |  | 0.27
28 |  |  |  | 0.28 |  |  | 0.28
29 |  |  |  | 0.3 |  |  | 0.3
30 |  |  |  | 0.32 |  |  | 0.32
31 |  |  |  | 0.28 |  |  | 0.28
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | 2022-11-03
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.5 | 50 | 125 | 13.5 | 7.8 | 47.9444 | yes | 7
2 | 2.2 | 50 | 110 | 16.4 | 7.7 | 36.8598 | yes | 7
3 | 2 | 50 | 100 | 18.5 | 7.7 | 31.3309 | yes | 7
4 | 2 | 50 | 100 | 16.1 | 7.8 | 38.1394 | yes | 7
5 | 2.1 | 50 | 105 | 14.2 | 7.8 | 43.7521 | yes | 7
6 | 2.3 | 50 | 115 | 19.2 | 7.6 | 29.8151 | yes | 7
7 | 2.6 | 50 | 130 | 13.9 | 7.7 | 45.5199 | yes | 7
8 | 2.6 | 50 | 130 | 14.6 | 7.7 | 43.4589 | yes | 7
9 | 2.5 | 50 | 125 | 15.8 | 7.7 | 39.6846 | yes | 7
10 | 2.5 | 50 | 125 | 16.2 | 7.7 | 38.6452 | yes | 7
11 | 2.4 | 50 | 120 | 14.1 | 7.7 | 43.9173 | yes | 7
12 | 2.3 | 50 | 115 | 17 | 7.7 | 35.8231 | yes | 7
13 | 2.1 | 50 | 105 | 21.4 | 7.6 | 25.1507 | yes | 7
14 | 2.5 | 50 | 125 | 19.4 | 7.6 | 30.0982 | yes | 7
15 | 2.4 | 50 | 120 | 19.7 | 7.6 | 29.1665 | yes | 7
16 | 2.4 | 50 | 120 | 18.6 | 7.6 | 31.3888 | yes | 7
17 | 2.3 | 50 | 115 | 19.1 | 7.6 | 30.0148 | yes | 7
18 | 2.5 | 50 | 125 | 16.8 | 7.7 | 37.1358 | yes | 7
19 | 2.6 | 50 | 130 | 13.9 | 7.7 | 45.5199 | yes | 7
20 | 2.5 | 50 | 125 | 12.6 | 7.8 | 50.882 | yes | 7
21 | 2.4 | 50 | 120 | 10.8 | 7.8 | 56.9327 | yes | 7
22 | 2.4 | 50 | 120 | 11.9 | 7.8 | 52.8668 | yes | 7
23 | 2.6 | 50 | 130 | 10.1 | 7.7 | 58.9299 | yes | 7
24 | 2.4 | 50 | 120 | 11.2 | 7.8 | 55.4163 | yes | 7
25 | 2.3 | 50 | 115 | 9.2 | 7.8 | 62.7256 | yes | 7
26 | 2.3 | 50 | 115 | 11.8 | 7.8 | 52.6146 | yes | 7
27 | 2.1 | 50 | 105 | 9.1 | 7.7 | 59.5072 | yes | 7
28 | 2.3 | 50 | 115 | 10.2 | 7.7 | 56.5337 | yes | 7
29 | 2.3 | 50 | 115 | 11.6 | 7.8 | 53.326 | yes | 7
30 | 2.2 | 50 | 110 | 11.1 | 7.8 | 54.5184 | yes | 7
31 | 2.2 | 50 | 110 | 10.1 | 7.8 | 58.3261 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2