## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-11-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.32 |  | 0.32
2 |  |  |  |  | 0.31 |  | 0.31
3 |  |  |  |  | 0.34 |  | 0.34
4 |  |  |  |  | 0.35 |  | 0.35
5 |  |  |  |  | 0.41 |  | 0.41
6 |  |  |  |  | 0.38 |  | 0.38
7 |  |  |  |  | 0.35 |  | 0.35
8 |  |  |  |  | 0.38 |  | 0.38
9 |  |  |  |  | 0.41 |  | 0.41
10 |  |  |  |  | 0.38 |  | 0.38
11 |  |  |  |  | 0.35 |  | 0.35
12 |  |  |  |  | 0.35 |  | 0.35
13 |  |  |  |  | 0.38 |  | 0.38
14 |  |  |  |  | 0.34 |  | 0.34
15 |  |  |  |  | 0.32 |  | 0.32
16 |  |  |  |  | 0.39 |  | 0.39
17 |  |  |  |  | 0.4 |  | 0.4
18 |  |  |  |  | 0.41 |  | 0.41
19 |  |  |  |  | 0.42 |  | 0.42
20 |  |  |  |  | 0.39 |  | 0.39
21 |  |  |  |  | 0.37 |  | 0.37
22 |  |  |  |  | 0.4 |  | 0.4
23 |  |  |  |  | 0.37 |  | 0.37
24 |  |  |  |  | 0.36 |  | 0.36
25 |  |  |  |  | 0.39 |  | 0.39
26 |  |  |  |  | 0.41 |  | 0.41
27 |  |  |  |  | 0.41 |  | 0.41
28 |  |  |  |  | 0.39 |  | 0.39
29 |  |  |  |  | 0.43 |  | 0.43
30 |  |  |  |  | 0.4 |  | 0.4
31 | [6 empty] | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:12/1/2022
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.3 | 50 | 115 | 9.6 | 7.8 | 61.0425 | yes | 7
2 | 2.5 | 50 | 125 | 10.2 | 7.8 | 59.9845 | yes | 7
3 | 2.5 | 50 | 125 | 11.3 | 7.8 | 55.6831 | yes | 7
4 | 2.3 | 50 | 115 | 9.6 | 7.8 | 61.0425 | yes | 7
5 | 2.4 | 50 | 120 | 9.3 | 7.7 | 60.7874 | yes | 7
6 | 2.3 | 50 | 115 | 10.6 | 7.7 | 55.0288 | yes | 7
7 | 2.2 | 50 | 110 | 10.3 | 7.8 | 57.5422 | yes | 7
8 | 2.4 | 50 | 120 | 10.1 | 7.8 | 59.6954 | yes | 7
9 | 2.3 | 50 | 115 | 9.1 | 7.7 | 60.9063 | yes | 7
10 | 2.6 | 50 | 130 | 8.8 | 7.9 | 69.2398 | yes | 7
11 | 2.3 | 50 | 115 | 8.4 | 7.7 | 63.8773 | yes | 7
12 | 2.4 | 50 | 120 | 9.6 | 7.7 | 59.5624 | yes | 7
13 | 2.4 | 50 | 120 | 10.5 | 7.7 | 56.0445 | yes | 7
14 | 2.5 | 50 | 125 | 10.7 | 7 | 43.6124 | yes | 7
15 | 2.3 | 50 | 115 | 11.6 | 7.7 | 51.4532 | yes | 7
16 | 2.3 | 50 | 115 | 11.9 | 7.8 | 52.2627 | yes | 7
17 | 2.2 | 50 | 110 | 12.7 | 7.8 | 48.8648 | yes | 7
18 | 2.1 | 50 | 105 | 11.4 | 7.8 | 52.8182 | yes | 7
19 | 2.4 | 50 | 120 | 9.4 | 7.7 | 60.3761 | yes | 7
20 | 2.3 | 50 | 115 | 10.5 | 7.8 | 57.4304 | yes | 7
21 | 2.5 | 50 | 125 | 9.2 | 7.7 | 61.9182 | yes | 7
22 | 2.4 | 50 | 120 | 9.9 | 7.7 | 58.364 | yes | 7
23 | 2.3 | 50 | 115 | 11.4 | 7.7 | 52.1476 | yes | 7
24 | 2.5 | 50 | 125 | 10.6 | 7.8 | 58.3803 | yes | 7
25 | 2.3 | 50 | 115 | 11.1 | 7.7 | 53.2084 | yes | 7
26 | 2.4 | 50 | 120 | 10.3 | 7.9 | 61.0595 | yes | 7
27 | 2.3 | 50 | 115 | 10.8 | 7.8 | 56.2781 | yes | 7
28 | 2.3 | 50 | 115 | 11 | 7.7 | 53.5671 | yes | 7
29 | 2.5 | 50 | 125 | 10.5 | 7.7 | 56.6961 | yes | 7
30 | 2.4 | 50 | 120 | 11.8 | 7.7 | 51.3541 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2