## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-12-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.28 |  | 0.28
2 |  |  |  |  | 0.32 |  | 0.32
3 |  |  |  |  | 0.34 |  | 0.34
4 |  |  |  |  | 0.36 |  | 0.36
5 |  |  |  |  | 0.33 |  | 0.33
6 |  |  |  |  | 0.38 |  | 0.38
7 |  |  |  |  | 0.4 |  | 0.4
8 |  |  |  |  | 0.42 |  | 0.42
9 |  |  |  |  | 0.52 |  | 0.52
10 |  |  |  |  | 0.36 |  | 0.36
11 |  |  |  |  | 0.31 |  | 0.31
12 |  |  |  |  | 0.34 |  | 0.34
13 |  |  |  |  | 0.29 |  | 0.29
14 |  |  |  |  | 0.31 |  | 0.31
15 |  |  |  |  | 0.3 |  | 0.3
16 |  |  |  |  | 0.33 |  | 0.33
17 |  |  |  |  | 0.34 |  | 0.34
18 |  |  |  |  | 0.31 |  | 0.31
19 |  |  |  |  | 0.56 |  | 0.56
20 |  |  |  |  | 0.57 |  | 0.57
21 |  |  |  |  | 0.56 |  | 0.56
22 |  |  |  |  | 0.54 |  | 0.54
23 |  |  |  |  | 0.86 |  | 0.86
24 |  |  |  |  | 0.85 |  | 0.85
25 |  |  |  |  | 0.81 |  | 0.81
26 |  |  |  |  | 0.86 |  | 0.86
27 |  |  |  |  | 0.76 |  | 0.76
28 |  |  |  |  | 0.69 |  | 0.69
29 |  |  |  |  | 0.71 |  | 0.71
30 |  |  |  |  | 0.78 |  | 0.78
31 |  |  |  |  | 0.77 |  | 0.77
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:1/2/2023
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.4 | 50 | 120 | 6.2 | 7.8 | 77.961 | yes | 7
2 | 2.5 | 50 | 125 | 7.7 | 7.8 | 71.1457 | yes | 7
3 | 2.6 | 50 | 130 | 6.9 | 7.8 | 76.0617 | yes | 7
4 | 2.4 | 50 | 120 | 7 | 7.9 | 76.5373 | yes | 7
5 | 2.4 | 50 | 120 | 7.8 | 7.8 | 69.834 | yes | 7
6 | 2.4 | 50 | 120 | 6.4 | 7.7 | 74.1204 | yes | 7
7 | 2.3 | 50 | 115 | 5.6 | 7.8 | 80.305 | yes | 7
8 | 2.3 | 50 | 115 | 5.8 | 7.8 | 79.2025 | yes | 7
9 | 2.3 | 50 | 115 | 6.2 | 7.8 | 77.0452 | yes | 7
10 | 2.4 | 50 | 120 | 7.8 | 7.9 | 72.436 | yes | 7
11 | 2.2 | 50 | 110 | 7.7 | 7.8 | 68.6832 | yes | 7
12 | 2.2 | 50 | 110 | 5.8 | 7.7 | 75.4467 | yes | 7
13 | 2.1 | 50 | 105 | 4.2 | 8.1 | 96.5814 | yes | 7
14 | 2 | 50 | 100 | 6.8 | 7.8 | 71.3602 | yes | 7
15 | 2.1 | 50 | 105 | 5.2 | 7.7 | 77.7107 | yes | 7
16 | 2.6 | 50 | 130 | 6.8 | 7.7 | 73.8276 | yes | 7
17 | 2.7 | 50 | 135 | 5 | 7.7 | 84.5978 | yes | 7
18 | 2.6 | 50 | 130 | 6.2 | 7.7 | 76.9433 | yes | 7
19 | 2.8 | 50 | 140 | 3.9 | 8 | 103.3266 | yes | 7
20 | 2.9 | 50 | 145 | 5.1 | 7.8 | 89.2774 | yes | 7
21 | 2.6 | 50 | 130 | 5.9 | 7.8 | 81.5009 | yes | 7
22 | 2.3 | 50 | 115 | 4.4 | 7.9 | 90.5626 | yes | 7
23 | 2 | 50 | 100 | 3.5 | 7.8 | 89.6438 | yes | 7
24 | 2.1 | 50 | 105 | 4.7 | 7.8 | 83.4648 | yes | 7
25 | 2.2 | 50 | 110 | 5.6 | 7.8 | 79.3601 | yes | 7
26 | 2 | 50 | 100 | 3.6 | 7.8 | 89.0226 | yes | 7
27 | 2.4 | 50 | 120 | 6.9 | 7.8 | 74.2884 | yes | 7
28 | 2.6 | 50 | 130 | 7.2 | 7.8 | 74.5059 | yes | 7
29 | 2.4 | 50 | 120 | 6.7 | 7.7 | 72.6067 | yes | 7
30 | 2.3 | 50 | 115 | 6.2 | 7.8 | 77.0452 | yes | 7
31 | 2.2 | 50 | 110 | 5.9 | 7.8 | 77.7328 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
PAGE 2 of 2