## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-01-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.62 |  | 0.62
2 |  |  |  |  | 0.66 |  | 0.66
3 |  |  |  |  | 0.76 |  | 0.76
4 |  |  |  |  | 0.88 |  | 0.88
5 |  |  |  |  | 0.81 |  | 0.81
6 |  |  |  |  | 0.83 |  | 0.83
7 |  |  |  |  | 0.86 |  | 0.86
8 |  |  |  |  | 0.84 |  | 0.84
9 |  |  |  |  | 0.88 |  | 0.88
10 |  |  |  |  | 0.85 |  | 0.85
11 |  |  |  |  | 0.78 |  | 0.78
12 |  |  |  |  | 0.9 |  | 0.9
13 |  |  |  |  | 0.88 |  | 0.88
14 |  |  |  |  | 0.87 |  | 0.87
15 |  |  |  |  | 0.83 |  | 0.83
16 |  |  |  |  | 0.87 |  | 0.87
17 |  |  |  |  | 0.83 |  | 0.83
18 |  |  |  |  | 0.93 |  | 0.93
19 |  |  |  |  | 0.89 |  | 0.89
20 |  |  |  |  | 0.92 |  | 0.92
21 |  |  |  |  | 0.95 |  | 0.95
22 |  |  |  |  | 0.93 |  | 0.93
23 |  |  |  |  | 0.91 |  | 0.91
24 |  |  |  |  | 0.96 |  | 0.96
25 |  |  |  |  | 0.92 |  | 0.92
26 |  |  |  |  | 0.94 |  | 0.94
27 |  |  |  |  | 0.88 |  | 0.88
28 |  |  |  |  | 0.86 |  | 0.86
29 |  |  |  |  | 0.88 |  | 0.88
30 |  |  |  |  | 0.92 |  | 0.92
31 |  |  |  |  | 0.87 |  | 0.87
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:2/6/2023
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 50 | 100 | 4.6 | 7.8 | 83.0539 | yes | 7
2 | 2.1 | 50 | 105 | 2.7 | 7.8 | 95.9189 | yes | 7
3 | 2.1 | 50 | 105 | 4.1 | 7.7 | 83.8539 | yes | 7
4 | 2.5 | 50 | 125 | 4.4 | 7.6 | 82.9987 | yes | 7
5 | 2.2 | 50 | 110 | 5.1 | 7.3 | 68.381 | yes | 7
6 | 2.2 | 50 | 110 | 6.2 | 7.3 | 63.4317 | yes | 7
7 | 2.1 | 50 | 105 | 6.9 | 7.4 | 61.9875 | yes | 7
8 | 2 | 50 | 100 | 7 | 7.5 | 63.1011 | yes | 7
9 | 2 | 50 | 100 | 7.2 | 7.5 | 62.248 | yes | 7
10 | 2.1 | 50 | 105 | 6 | 7.5 | 68.3553 | yes | 7
11 | 2 | 50 | 100 | 6.2 | 7.5 | 66.6411 | yes | 7
12 | 2.9 | 50 | 145 | 7.2 | 7.6 | 71.7304 | yes | 7
13 | 2.8 | 50 | 140 | 8.3 | 7.6 | 65.7489 | yes | 7
14 | 2.9 | 50 | 145 | 8.4 | 7.6 | 66.0696 | yes | 7
15 | 2.7 | 50 | 135 | 8.8 | 7.6 | 62.8075 | yes | 7
16 | 2.5 | 50 | 125 | 7.6 | 7.6 | 66.5912 | yes | 7
17 | 2.2 | 50 | 110 | 6.9 | 7.6 | 67.445 | yes | 7
18 | 2.2 | 50 | 110 | 7.2 | 7.6 | 66.0758 | yes | 7
19 | 2.3 | 50 | 115 | 6.9 | 7.6 | 68.24 | yes | 7
20 | 2.1 | 50 | 105 | 7.6 | 7.6 | 63.5502 | yes | 7
21 | 2 | 50 | 100 | 4.6 | 7.6 | 77.1545 | yes | 7
22 | 2.1 | 50 | 105 | 5.4 | 7.6 | 73.8832 | yes | 7
23 | 2.2 | 50 | 110 | 5.2 | 7.7 | 78.6349 | yes | 7
24 | 2 | 50 | 100 | 4.5 | 7.7 | 80.6022 | yes | 7
25 | 2.1 | 50 | 105 | 5.2 | 7.7 | 77.7107 | yes | 7
26 | 2.1 | 50 | 105 | 4 | 7.7 | 84.4373 | yes | 7
27 | 2.2 | 50 | 110 | 4.8 | 7.7 | 80.8393 | yes | 7
28 | 2.6 | 50 | 130 | 5.2 | 7.7 | 82.4493 | yes | 7
29 | 2.9 | 50 | 145 | 4.1 | 7.7 | 92.2272 | yes | 7
30 | 2.9 | 50 | 145 | 3.4 | 7.8 | 100.5135 | yes | 7
31 | 2.9 | 50 | 145 | 2.3 | 7.8 | 108.5633 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
2.9