## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-04-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.95 |  | 0.95
2 |  |  |  |  | 0.89 |  | 0.89
3 |  |  |  |  | 0.9 |  | 0.9
4 |  |  |  |  | 0.92 |  | 0.92
5 |  |  |  |  | 0.91 |  | 0.91
6 |  |  |  |  | 0.92 |  | 0.92
7 |  |  |  |  | 0.94 |  | 0.94
8 |  |  |  |  | 0.9 |  | 0.9
9 |  |  |  |  | 0.94 |  | 0.94
10 |  |  |  |  | 0.92 |  | 0.92
11 |  |  |  |  | 0.94 |  | 0.94
12 |  |  |  |  | 0.92 |  | 0.92
13 |  |  |  |  | 0.94 |  | 0.94
14 |  |  |  |  | 0.96 |  | 0.96
15 |  |  |  |  | 0.94 |  | 0.94
16 |  |  |  |  | 0.9 |  | 0.9
17 |  |  |  |  | 0.92 |  | 0.92
18 |  |  |  |  | 0.96 |  | 0.96
19 |  |  |  |  | 0.88 |  | 0.88
20 |  |  |  |  | 0.87 |  | 0.87
21 |  |  |  |  | 0.85 |  | 0.85
22 |  |  |  |  | 0.92 |  | 0.92
23 |  |  |  |  | 0.94 |  | 0.94
24 |  |  |  |  | 0.9 |  | 0.9
25 |  |  |  |  | 0.96 |  | 0.96
26 |  |  |  |  | 0.94 |  | 0.94
27 |  |  |  |  | 0.92 |  | 0.92
28 |  |  |  |  | 0.96 |  | 0.96
29 |  |  |  |  | 0.94 |  | 0.94
30 |  |  |  |  | 0.9 |  | 0.9
31 | [6 empty] | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE:5/2/2023
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3 | 50 | 150 | 5.5 | 7.7 | 84.6782 | yes | 7
2 | 2.9 | 50 | 145 | 6.2 | 7.7 | 79.7215 | yes | 7
3 | 2.6 | 50 | 130 | 5.8 | 7.8 | 82.067 | yes | 7
4 | 2.4 | 50 | 120 | 4.8 | 7.8 | 85.8939 | yes | 7
5 | 2.9 | 50 | 145 | 3.9 | 7.8 | 97.0628 | yes | 7
6 | 2.9 | 50 | 145 | 7 | 7.6 | 72.723 | yes | 7
7 | 3 | 50 | 150 | 8.7 | 7.6 | 65.4911 | yes | 7
8 | 2.9 | 50 | 145 | 8.4 | 7.7 | 68.5222 | yes | 7
9 | 2.9 | 50 | 145 | 9.3 | 7.7 | 64.4345 | yes | 7
10 | 3 | 50 | 150 | 8.8 | 7.6 | 65.0456 | yes | 7
11 | 2.9 | 50 | 145 | 7.8 | 7.6 | 68.838 | yes | 7
12 | 2.8 | 50 | 140 | 4.2 | 7.6 | 87.2109 | yes | 7
13 | 2.8 | 50 | 140 | 7.8 | 7.8 | 73.1972 | yes | 7
14 | 3 | 50 | 150 | 5.5 | 7.7 | 84.6782 | yes | 7
15 | 3 | 50 | 150 | 9.9 | 7.6 | 60.3537 | yes | 7
16 | 2.8 | 50 | 140 | 8.8 | 7.6 | 63.5443 | yes | 7
17 | 2.9 | 50 | 145 | 5.9 | 7.7 | 81.3928 | yes | 7
18 | 2.8 | 50 | 140 | 5.8 | 7.7 | 80.9927 | yes | 7
19 | 2.9 | 50 | 145 | 6.1 | 7.7 | 80.2746 | yes | 7
20 | 2.7 | 50 | 135 | 7.8 | 7.7 | 69.7422 | yes | 7
21 | 2.5 | 50 | 125 | 7 | 7.7 | 71.967 | yes | 7
22 | 2.3 | 50 | 115 | 9.5 | 7.7 | 59.2755 | yes | 7
23 | 2.1 | 50 | 105 | 12.8 | 7.8 | 47.998 | yes | 7
24 | 2.1 | 50 | 105 | 13.2 | 7.8 | 46.7452 | yes | 7
25 | 2.2 | 50 | 110 | 6.4 | 7.8 | 75.0986 | yes | 7
26 | 2.4 | 50 | 120 | 8.6 | 7.8 | 66.1129 | yes | 7
27 | 2.3 | 50 | 115 | 10.4 | 7.8 | 57.8201 | yes | 7
28 | 2.3 | 50 | 115 | 11.2 | 7.7 | 52.8522 | yes | 7
29 | 2.2 | 50 | 110 | 10 | 7.8 | 58.7224 | yes | 7
30 | 2.1 | 50 | 105 | 9.9 | 7.8 | 58.4398 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
2.9