## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-05-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.92 |  | 0.92
2 |  |  |  |  | 0.94 |  | 0.94
3 |  |  |  |  | 0.84 |  | 0.84
4 |  |  |  |  | 0.81 |  | 0.81
5 |  |  |  |  | 0.51 |  | 0.51
6 |  |  |  |  | 0.5 |  | 0.5
7 |  |  |  |  | 0.47 |  | 0.47
8 |  |  |  |  | 0.57 |  | 0.57
9 |  |  |  |  | 0.61 |  | 0.61
10 |  |  |  |  | 0.5 |  | 0.5
11 |  |  |  |  | 0.4 |  | 0.4
12 |  |  |  |  | 0.42 |  | 0.42
13 |  |  |  |  | 0.38 |  | 0.38
14 |  |  |  |  | 0.4 |  | 0.4
15 |  |  |  |  | 0.42 |  | 0.42
16 |  |  |  |  | 0.34 |  | 0.34
17 |  |  |  |  | 0.35 |  | 0.35
18 |  |  |  |  | 0.36 |  | 0.36
19 |  |  |  |  | 0.34 |  | 0.34
20 |  |  |  |  | 0.35 |  | 0.35
21 |  |  |  |  | 0.36 |  | 0.36
22 |  |  |  |  | 0.33 |  | 0.33
23 |  |  |  |  | 0.38 |  | 0.38
24 |  |  |  |  | 0.41 |  | 0.41
25 |  |  |  |  | 0.34 |  | 0.34
26 |  |  |  |  | 0.37 |  | 0.37
27 |  |  |  |  | 0.32 |  | 0.32
28 |  |  |  |  | 0.3 |  | 0.3
29 |  |  |  |  | 0.31 |  | 0.31
30 |  |  |  |  | 0.3 |  | 0.3
31 |  |  |  |  | 0.28 |  | 0.28
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 6/3/2023
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.1 | 50 | 105 | 11.1 | 7.9 | 55.8635 | yes | 7
2 | 2 | 50 | 100 | 13 | 7.9 | 48.5873 | yes | 7
3 | 2.5 | 50 | 125 | 13.6 | 7.9 | 49.4093 | yes | 7
4 | 2.4 | 50 | 120 | 11.9 | 7.9 | 54.7957 | yes | 7
5 | 2.6 | 50 | 130 | 10.3 | 7.8 | 60.2752 | yes | 7
6 | 2.4 | 50 | 120 | 9.6 | 7.8 | 61.757 | yes | 7
7 | 2.3 | 50 | 115 | 10 | 7.8 | 59.4078 | yes | 7
8 | 2.1 | 50 | 105 | 14.2 | 7.8 | 43.7521 | yes | 7
9 | 2.2 | 50 | 110 | 13.8 | 7.7 | 43.7967 | yes | 7
10 | 2.2 | 50 | 110 | 17.1 | 7.7 | 35.1839 | yes | 7
11 | 2.4 | 50 | 120 | 17 | 7.7 | 36.2321 | yes | 7
12 | 2.5 | 50 | 125 | 19.1 | 7.7 | 31.8657 | yes | 7
13 | 2.5 | 50 | 125 | 21.6 | 7.7 | 26.964 | yes | 7
14 | 2.2 | 50 | 110 | 24 | 7.7 | 22.1729 | yes | 7
15 | 2 | 50 | 100 | 24.5 | 7.8 | 21.7493 | yes | 7
16 | 2.1 | 50 | 105 | 17.5 | 7.8 | 35.1479 | yes | 7
17 | 2 | 50 | 100 | 24.8 | 7.7 | 20.5289 | yes | 7
18 | 2.2 | 50 | 110 | 16.1 | 7.8 | 39.0139 | yes | 7
19 | 2.1 | 50 | 105 | 15.6 | 7.8 | 39.8754 | yes | 7
20 | 2.2 | 50 | 110 | 17.8 | 7.8 | 34.8471 | yes | 7
21 | 2.4 | 50 | 120 | 20.5 | 7.8 | 29.7784 | yes | 7
22 | 2.3 | 50 | 115 | 21.6 | 7.8 | 27.3528 | yes | 7
23 | 2.2 | 50 | 110 | 18.3 | 7.7 | 32.4826 | yes | 7
24 | 2.3 | 50 | 115 | 15.6 | 7.8 | 40.7889 | yes | 7
25 | 2.3 | 50 | 115 | 18.3 | 7.8 | 34.092 | yes | 7
26 | 2.2 | 50 | 110 | 21.4 | 7.9 | 28.4438 | yes | 7
27 | 2.1 | 50 | 105 | 18.6 | 7.9 | 33.8971 | yes | 7
28 | 2.2 | 50 | 110 | 14.3 | 7.9 | 45.6034 | yes | 7
29 | 2.1 | 50 | 105 | 17.4 | 7.9 | 36.7131 | yes | 7
30 | 2.1 | 50 | 105 | 16.3 | 7.9 | 39.4947 | yes | 7
31 | 2 | 50 | 100 | 14.5 | 7.9 | 43.9979 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
2.9