## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-06-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.3 |  | 0.3
2 |  |  |  |  | 0.32 |  | 0.32
3 |  |  |  |  | 0.34 |  | 0.34
4 |  |  |  |  | 0.3 |  | 0.3
5 |  |  |  |  | 0.36 |  | 0.36
6 |  |  |  |  | 0.35 |  | 0.35
7 |  |  |  |  | 0.34 |  | 0.34
8 |  |  |  |  | 0.32 |  | 0.32
9 |  |  |  |  | 0.34 |  | 0.34
10 |  |  |  |  | 0.32 |  | 0.32
11 |  |  |  |  | 0.3 |  | 0.3
12 |  |  |  |  | 0.32 |  | 0.32
13 |  |  |  |  | 0.34 |  | 0.34
14 |  |  |  |  | 0.36 |  | 0.36
15 |  |  |  |  | 0.4 |  | 0.4
16 |  |  |  |  | 0.38 |  | 0.38
17 |  |  |  |  | 0.42 |  | 0.42
18 |  |  |  |  | 0.41 |  | 0.41
19 |  |  |  |  | 0.52 |  | 0.52
20 |  |  |  |  | 0.48 |  | 0.48
21 |  |  |  |  | 0.36 |  | 0.36
22 |  |  |  |  | 0.34 |  | 0.34
23 |  |  |  |  | 0.36 |  | 0.36
24 |  |  |  |  | 0.38 |  | 0.38
25 |  |  |  |  | 0.62 |  | 0.62
26 |  |  |  |  | 0.54 |  | 0.54
27 |  |  |  |  | 0.48 |  | 0.48
28 |  |  |  |  | 0.52 |  | 0.52
29 |  |  |  |  | 0.54 |  | 0.54
30 |  |  |  |  | 0.38 |  | 0.38
31 | [6 empty] | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 7/1/2023
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 50 | 110 | 16.2 | 7.8 | 38.7558 | yes | 7
2 | 2.2 | 50 | 110 | 14 | 7.8 | 44.8392 | yes | 7
3 | 2.4 | 50 | 120 | 14.8 | 7.8 | 43.4988 | yes | 7
4 | 2.5 | 50 | 125 | 16.6 | 7.9 | 40.5111 | yes | 7
5 | 2.5 | 50 | 125 | 15.2 | 7.9 | 44.4483 | yes | 7
6 | 2.4 | 50 | 120 | 15.6 | 7.8 | 41.2533 | yes | 7
7 | 2.3 | 50 | 115 | 14.8 | 7.9 | 44.6206 | yes | 7
8 | 2.3 | 50 | 115 | 13.2 | 7.8 | 47.8129 | yes | 7
9 | 2.4 | 50 | 120 | 16.6 | 7.8 | 38.6057 | yes | 7
10 | 2.4 | 50 | 120 | 15.8 | 7.9 | 42.2364 | yes | 7
11 | 2.3 | 50 | 115 | 16.2 | 7.9 | 40.6684 | yes | 7
12 | 2.2 | 50 | 110 | 15.6 | 7.9 | 41.8421 | yes | 7
13 | 2.2 | 50 | 110 | 16.5 | 7.9 | 39.4182 | yes | 7
14 | 2.2 | 50 | 110 | 14.3 | 7.9 | 45.6034 | yes | 7
15 | 2.3 | 50 | 115 | 13.8 | 7.9 | 47.6721 | yes | 7
16 | 2.3 | 50 | 115 | 16.5 | 7.8 | 38.4248 | yes | 7
17 | 2.2 | 50 | 110 | 15.8 | 7.8 | 39.7982 | yes | 7
18 | 2.2 | 50 | 110 | 14.2 | 7.8 | 44.2495 | yes | 7
19 | 2.1 | 50 | 105 | 13.5 | 7.8 | 45.8268 | yes | 7
20 | 2.2 | 50 | 110 | 14.4 | 7.8 | 43.6675 | yes | 7
21 | 2.1 | 50 | 105 | 15.2 | 7.8 | 40.9473 | yes | 7
22 | 2.3 | 50 | 115 | 16.6 | 7.8 | 38.1706 | yes | 7
23 | 2.4 | 50 | 120 | 15.8 | 7.9 | 42.2364 | yes | 7
24 | 2.3 | 50 | 115 | 13.8 | 7.9 | 47.6721 | yes | 7
25 | 2.9 | 50 | 145 | 20 | 7.9 | 33.8208 | yes | 7
26 | 2.8 | 50 | 140 | 20.6 | 7.9 | 32.1282 | yes | 7
27 | 2.8 | 50 | 140 | 21.2 | 7.9 | 30.8681 | yes | 7
28 | 2.4 | 50 | 120 | 24.7 | 7.9 | 23.325 | yes | 7
29 | 2.3 | 50 | 115 | 26.2 | 7.9 | 20.8406 | yes | 7
30 | 2.6 | 50 | 130 | 16.9 | 7.9 | 40.1654 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 | [5 empty] | Revised February 2012
2.9