## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-10-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.32 |  | 0.32
2 |  |  |  |  | 0.36 |  | 0.36
3 |  |  |  |  | 0.38 |  | 0.38
4 |  |  |  |  | 0.41 |  | 0.41
5 |  |  |  |  | 0.28 |  | 0.28
6 |  |  |  |  | 0.26 |  | 0.26
7 |  |  |  |  | 0.32 |  | 0.32
8 |  |  |  |  | 0.34 |  | 0.34
9 |  |  |  |  | 0.3 |  | 0.3
10 |  |  |  |  | 0.32 |  | 0.32
11 |  |  |  |  | 0.29 |  | 0.29
12 |  |  |  |  | 0.27 |  | 0.27
13 |  |  |  |  | 0.28 |  | 0.28
14 |  |  |  |  | 0.3 |  | 0.3
15 |  |  |  |  | 0.32 |  | 0.32
16 |  |  |  |  | 0.3 |  | 0.3
17 |  |  |  |  | 0.34 |  | 0.34
18 |  |  |  |  | 0.36 |  | 0.36
19 |  |  |  |  | 0.37 |  | 0.37
20 |  |  |  |  | 0.36 |  | 0.36
21 |  |  |  |  | 0.38 |  | 0.38
22 |  |  |  |  | 0.34 |  | 0.34
23 |  |  |  |  | 0.33 |  | 0.33
24 |  |  |  |  | 0.29 |  | 0.29
25 |  |  |  |  | 0.32 |  | 0.32
26 |  |  |  |  | 0.28 |  | 0.28
27 |  |  |  |  | 0.27 |  | 0.27
28 |  |  |  |  | 0.32 |  | 0.32
29 |  |  |  |  | 0.37 |  | 0.37
30 |  |  |  |  | 0.31 |  | 0.31
31 |  |  |  |  | 0.28 |  | 0.28
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 11/3/2023
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.3 | 50 | 115 | 16.2 | 7.7 | 37.7788 | yes | 7
2 | 2.2 | 50 | 110 | 14.9 | 7.7 | 40.7182 | yes | 7
3 | 2 | 50 | 100 | 15.9 | 7.7 | 37.2498 | yes | 7
4 | 2.1 | 50 | 105 | 14.2 | 7.7 | 42.1719 | yes | 7
5 | 2.2 | 50 | 110 | 14.6 | 7.5 | 38.586 | yes | 7
6 | 2.4 | 50 | 120 | 15.2 | 7.6 | 39.3539 | yes | 7
7 | 2.3 | 50 | 115 | 15.6 | 7.5 | 36.5185 | yes | 7
8 | 2.4 | 50 | 120 | 14.8 | 7.6 | 40.412 | yes | 7
9 | 2.2 | 50 | 110 | 14.7 | 7.8 | 42.8084 | yes | 7
10 | 2.3 | 50 | 115 | 14 | 7.8 | 45.3488 | yes | 7
11 | 2.3 | 50 | 115 | 13.8 | 7.8 | 45.9529 | yes | 7
12 | 2.2 | 50 | 110 | 13.2 | 7.8 | 47.2761 | yes | 7
13 | 2.1 | 50 | 105 | 11.2 | 7.7 | 51.6519 | yes | 7
14 | 2.3 | 50 | 115 | 12.3 | 7.8 | 50.8806 | yes | 7
15 | 2.4 | 50 | 120 | 12.6 | 7.8 | 50.3113 | yes | 7
16 | 2.2 | 50 | 110 | 11.8 | 7.8 | 52.0136 | yes | 7
17 | 2.3 | 50 | 115 | 12.6 | 7.8 | 49.7469 | yes | 7
18 | 2.1 | 50 | 105 | 11.8 | 7.8 | 51.4201 | yes | 7
19 | 2 | 50 | 100 | 11.3 | 7.8 | 52.5662 | yes | 7
20 | 2.3 | 50 | 115 | 12.6 | 7.8 | 49.7469 | yes | 7
21 | 2.5 | 50 | 125 | 13.8 | 7.8 | 47.0028 | yes | 7
22 | 2.6 | 50 | 130 | 14.5 | 7.8 | 45.3858 | yes | 7
23 | 2.7 | 50 | 135 | 13.3 | 7.9 | 51.548 | yes | 7
24 | 2.6 | 50 | 130 | 12.8 | 7.9 | 52.6806 | yes | 7
25 | 2.5 | 50 | 125 | 11.7 | 7.7 | 52.2963 | yes | 7
26 | 2.7 | 50 | 135 | 12.1 | 7.8 | 53.9932 | yes | 7
27 | 2.4 | 50 | 120 | 12.6 | 7.8 | 50.3113 | yes | 7
28 | 2.3 | 50 | 115 | 13 | 7.7 | 46.7024 | yes | 7
29 | 2.2 | 50 | 110 | 10.6 | 7.8 | 56.3875 | yes | 7
30 | 2.5 | 50 | 125 | 10 | 7.8 | 60.8044 | yes | 7
31 | 2.6 | 50 | 130 | 9.4 | 7.8 | 64.0804 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  |  |  | 98.2774 | Revised February 2012