## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-12-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.31 |  | 0.31
2 |  |  |  |  | 0.38 |  | 0.38
3 |  |  |  |  | 0.3 |  | 0.3
4 |  |  |  |  | 0.32 |  | 0.32
5 |  |  |  |  | 0.34 |  | 0.34
6 |  |  |  |  | 0.41 |  | 0.41
7 |  |  |  |  | 0.43 |  | 0.43
8 |  |  |  |  | 0.5 |  | 0.5
9 |  |  |  |  | 0.52 |  | 0.52
10 |  |  |  |  | 0.49 |  | 0.49
11 |  |  |  |  | 0.5 |  | 0.5
12 |  |  |  |  | 0.48 |  | 0.48
13 |  |  |  |  | 0.68 |  | 0.68
14 |  |  |  |  | 0.73 |  | 0.73
15 |  |  |  |  | 0.81 |  | 0.81
16 |  |  |  |  | 0.82 |  | 0.82
17 |  |  |  |  | 0.78 |  | 0.78
18 |  |  |  |  | 0.8 |  | 0.8
19 |  |  |  |  | 0.78 |  | 0.78
20 |  |  |  |  | 0.82 |  | 0.82
21 |  |  |  |  | 0.76 |  | 0.76
22 |  |  |  |  | 0.78 |  | 0.78
23 |  |  |  |  | 0.72 |  | 0.72
24 |  |  |  |  | 0.78 |  | 0.78
25 |  |  |  |  | 0.76 |  | 0.76
26 |  |  |  |  | 0.78 |  | 0.78
27 |  |  |  |  | 0.82 |  | 0.82
28 |  |  |  |  | 0.85 |  | 0.85
29 |  |  |  |  | 0.93 |  | 0.93
30 |  |  |  |  | 0.9 |  | 0.9
31 |  |  |  |  | 0.92 |  | 0.92
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 1/3/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.6 | 50 | 130 | 5.9 | 7.6 | 75.7178 | yes | 7
2 | 2.4 | 50 | 120 | 5.9 | 7.6 | 73.9529 | yes | 7
3 | 2.4 | 50 | 120 | 8.4 | 7.6 | 62.3234 | yes | 7
4 | 2.3 | 50 | 115 | 8.8 | 7.6 | 59.9511 | yes | 7
5 | 2.3 | 50 | 115 | 9 | 7.6 | 59.1436 | yes | 7
6 | 2.8 | 50 | 140 | 8 | 7.7 | 69.6048 | yes | 7
7 | 3 | 50 | 150 | 7.7 | 7.8 | 75.4609 | yes | 7
8 | 3 | 50 | 150 | 7.2 | 7.8 | 78.1086 | yes | 7
9 | 2.8 | 50 | 140 | 8.1 | 7.8 | 71.7034 | yes | 7
10 | 2.6 | 50 | 130 | 6.3 | 7.8 | 79.2775 | yes | 7
11 | 2.7 | 50 | 135 | 6.4 | 7.8 | 79.6687 | yes | 7
12 | 2.8 | 50 | 140 | 7.6 | 7.8 | 74.2114 | yes | 7
13 | 2.7 | 50 | 135 | 7 | 7.8 | 76.4361 | yes | 7
14 | 2.8 | 50 | 140 | 7.7 | 7.7 | 71.0521 | yes | 7
15 | 2.7 | 50 | 135 | 6.5 | 7.6 | 73.5151 | yes | 7
16 | 2.8 | 50 | 140 | 6 | 7.6 | 76.9942 | yes | 7
17 | 2.8 | 50 | 140 | 5.4 | 7.6 | 80.2518 | yes | 7
18 | 2.7 | 50 | 135 | 5.2 | 7.6 | 80.4116 | yes | 7
19 | 2.8 | 50 | 140 | 5.8 | 7.6 | 78.0643 | yes | 7
20 | 2.8 | 50 | 140 | 5.6 | 7.6 | 79.15 | yes | 7
21 | 2.8 | 50 | 140 | 4.6 | 7.7 | 88.0197 | yes | 7
22 | 2.9 | 50 | 145 | 4.8 | 7.7 | 87.8439 | yes | 7
23 | 3 | 50 | 150 | 4 | 7.7 | 93.9867 | yes | 7
24 | 2.9 | 50 | 145 | 3.8 | 7.7 | 94.1754 | yes | 7
25 | 2.8 | 50 | 140 | 4.2 | 7.7 | 90.5022 | yes | 7
26 | 2.8 | 50 | 140 | 4 | 7.7 | 91.7708 | yes | 7
27 | 2.8 | 50 | 140 | 6 | 7.7 | 79.8802 | yes | 7
28 | 2.5 | 50 | 125 | 7 | 7.7 | 71.967 | yes | 7
29 | 2.2 | 50 | 110 | 8 | 7.6 | 62.5679 | yes | 7
30 | 2.6 | 50 | 130 | 9 | 7.6 | 61.2416 | yes | 7
31 | 2.4 | 50 | 120 | 8.4 | 7.6 | 62.3234 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012