## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-01-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.9 |  | 0.9
2 |  |  |  |  | 0.94 |  | 0.94
3 |  |  |  |  | 0.88 |  | 0.88
4 |  |  |  |  | 0.86 |  | 0.86
5 |  |  |  |  | 0.91 |  | 0.91
6 |  |  |  |  | 0.88 |  | 0.88
7 |  |  |  |  | 0.91 |  | 0.91
8 |  |  |  |  | 0.91 |  | 0.91
9 |  |  |  |  | 0.82 |  | 0.82
10 |  |  |  |  | 0.8 |  | 0.8
11 |  |  |  |  | 0.81 |  | 0.81
12 |  |  |  |  | 0.84 |  | 0.84
13 |  |  |  |  | 0.8 |  | 0.8
14 |  |  |  |  | 0.78 |  | 0.78
15 |  |  |  |  | 0.82 |  | 0.82
16 |  |  |  |  | 0.8 |  | 0.8
17 |  |  |  |  | 0.78 |  | 0.78
18 |  |  |  |  | 0.8 |  | 0.8
19 |  |  |  |  | 0.76 |  | 0.76
20 |  |  |  |  | 0.78 |  | 0.78
21 |  |  |  |  | 0.82 |  | 0.82
22 |  |  |  |  | 0.84 |  | 0.84
23 |  |  |  |  | 0.82 |  | 0.82
24 |  |  |  |  | 0.84 |  | 0.84
25 |  |  |  |  | 0.8 |  | 0.8
26 |  |  |  |  | 0.78 |  | 0.78
27 |  |  |  |  | 0.81 |  | 0.81
28 |  |  |  |  | 0.82 |  | 0.82
29 |  |  |  |  | 0.88 |  | 0.88
30 |  |  |  |  | 0.9 |  | 0.9
31 |  |  |  |  | 0.78 |  | 0.78
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 2/2/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.3 | 50 | 115 | 6.2 | 7.7 | 74.2674 | yes | 7
2 | 2.1 | 50 | 105 | 5.8 | 7.7 | 74.5621 | yes | 7
3 | 2.2 | 50 | 110 | 6.6 | 7.7 | 71.4072 | yes | 7
4 | 2.2 | 50 | 110 | 7.7 | 7.7 | 66.2244 | yes | 7
5 | 3 | 50 | 150 | 9.6 | 7.5 | 59.4078 | yes | 7
6 | 2.9 | 50 | 145 | 7.2 | 7.6 | 71.7304 | yes | 7
7 | 2.8 | 50 | 140 | 6.5 | 7.6 | 74.3865 | yes | 7
8 | 2.8 | 50 | 140 | 6.6 | 7.6 | 73.8763 | yes | 7
9 | 2.9 | 50 | 145 | 4.3 | 7.7 | 90.9519 | yes | 7
10 | 2.8 | 50 | 140 | 5.2 | 7.7 | 84.4292 | yes | 7
11 | 2.8 | 50 | 140 | 5.6 | 7.7 | 82.1215 | yes | 7
12 | 2.7 | 50 | 135 | 4.8 | 7.7 | 85.7797 | yes | 7
13 | 2.7 | 50 | 135 | 3.4 | 7.7 | 94.554 | yes | 7
14 | 2.6 | 50 | 130 | 2.4 | 7.7 | 100.1867 | yes | 7
15 | 2.8 | 50 | 140 | 2.1 | 7.7 | 104.7939 | yes | 7
16 | 2.7 | 50 | 135 | 1.1 | 7.7 | 111.0653 | yes | 7
17 | 2.9 | 50 | 145 | 1.1 | 7.8 | 118.1144 | yes | 7
18 | 2.6 | 50 | 130 | 2.6 | 7.8 | 102.5468 | yes | 7
19 | 2.8 | 50 | 140 | 2.8 | 7.7 | 99.7846 | yes | 7
20 | 2.7 | 50 | 135 | 3.4 | 7.7 | 94.554 | yes | 7
21 | 2.8 | 50 | 140 | 4.1 | 7.6 | 87.8188 | yes | 7
22 | 2.7 | 50 | 135 | 5 | 7.6 | 81.5318 | yes | 7
23 | 2.6 | 50 | 130 | 5.3 | 7.6 | 78.9182 | yes | 7
24 | 2.6 | 50 | 130 | 6.4 | 7.7 | 75.8895 | yes | 7
25 | 2.7 | 50 | 135 | 7.2 | 7.7 | 72.6751 | yes | 7
26 | 2.6 | 50 | 130 | 7.7 | 7.7 | 69.4025 | yes | 7
27 | 2.6 | 50 | 130 | 9.2 | 7.7 | 62.6438 | yes | 7
28 | 2.7 | 50 | 135 | 8.8 | 7.7 | 65.1308 | yes | 7
29 | 2.8 | 50 | 140 | 8.9 | 7.7 | 65.4483 | yes | 7
30 | 2.9 | 50 | 145 | 9.6 | 7.7 | 63.1306 | yes | 7
31 | 2.9 | 50 | 145 | 9.3 | 7.7 | 64.4345 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012