## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-02-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.72 |  | 0.72
2 |  |  |  |  | 0.69 |  | 0.69
3 |  |  |  |  | 0.81 |  | 0.81
4 |  |  |  |  | 0.84 |  | 0.84
5 |  |  |  |  | 0.92 |  | 0.92
6 |  |  |  |  | 0.91 |  | 0.91
7 |  |  |  |  | 0.9 |  | 0.9
8 |  |  |  |  | 0.88 |  | 0.88
9 |  |  |  |  | 0.9 |  | 0.9
10 |  |  |  |  | 0.92 |  | 0.92
11 |  |  |  |  | 0.96 |  | 0.96
12 |  |  |  |  | 0.91 |  | 0.91
13 |  |  |  |  | 0.93 |  | 0.93
14 |  |  |  |  | 0.9 |  | 0.9
15 |  |  |  |  | 0.93 |  | 0.93
16 |  |  |  |  | 0.93 |  | 0.93
17 |  |  |  |  | 0.96 |  | 0.96
18 |  |  |  |  | 0.92 |  | 0.92
19 |  |  |  |  | 0.9 |  | 0.9
20 |  |  |  |  | 0.92 |  | 0.92
21 |  |  |  |  | 0.96 |  | 0.96
22 |  |  |  |  | 0.9 |  | 0.9
23 |  |  |  |  | 0.91 |  | 0.91
24 |  |  |  |  | 0.78 |  | 0.78
25 |  |  |  |  | 0.76 |  | 0.76
26 |  |  |  |  | 0.74 |  | 0.74
27 |  |  |  |  | 0.62 |  | 0.62
28 |  |  |  |  | 0.54 |  | 0.54
29 |  |  |  |  | 0.57 |  | 0.57
30 |  |  |  |  | 0 |  | 0
31 |  |  |  |  | 0 |  | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 3/4/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.8 | 50 | 140 | 8.7 | 7.7 | 66.3485 | yes | 7
2 | 2.7 | 50 | 135 | 8.1 | 7.7 | 68.3233 | yes | 7
3 | 2.8 | 50 | 140 | 9.2 | 7.7 | 64.1223 | yes | 7
4 | 2.9 | 50 | 145 | 9.9 | 7.7 | 61.8548 | yes | 7
5 | 2.8 | 50 | 140 | 7.7 | 7.7 | 71.0521 | yes | 7
6 | 2.8 | 50 | 140 | 8.2 | 7.7 | 68.6574 | yes | 7
7 | 2.4 | 50 | 120 | 6.1 | 7.7 | 75.6677 | yes | 7
8 | 2.1 | 50 | 105 | 5.5 | 7.7 | 76.1192 | yes | 7
9 | 2.1 | 50 | 105 | 6.1 | 7.7 | 73.0387 | yes | 7
10 | 2.2 | 50 | 110 | 6.9 | 7.7 | 69.9522 | yes | 7
11 | 2.1 | 50 | 105 | 6.3 | 7.8 | 74.7311 | yes | 7
12 | 2 | 50 | 100 | 7.2 | 7.8 | 69.4286 | yes | 7
13 | 2.1 | 50 | 105 | 4.5 | 7.8 | 84.63 | yes | 7
14 | 2.2 | 50 | 110 | 4.2 | 7.8 | 87.4436 | yes | 7
15 | 2.2 | 50 | 110 | 5.3 | 7.8 | 81.0234 | yes | 7
16 | 2.3 | 50 | 115 | 5.1 | 7.8 | 83.1327 | yes | 7
17 | 2.7 | 50 | 135 | 5.2 | 7.8 | 86.5745 | yes | 7
18 | 3 | 50 | 150 | 6.5 | 7.7 | 79.0153 | yes | 7
19 | 2.3 | 50 | 115 | 6 | 7.8 | 78.1159 | yes | 7
20 | 2.1 | 50 | 105 | 6.8 | 7.8 | 72.2045 | yes | 7
21 | 2.8 | 50 | 140 | 7.6 | 7.8 | 74.2114 | yes | 7
22 | 2.1 | 50 | 105 | 7 | 7.8 | 71.2194 | yes | 7
23 | 2.2 | 50 | 110 | 6.2 | 7.8 | 76.1407 | yes | 7
24 | 2.9 | 50 | 145 | 10.5 | 7.8 | 61.5732 | yes | 7
25 | 2.8 | 50 | 140 | 8.9 | 7.8 | 67.8762 | yes | 7
26 | 2.9 | 50 | 145 | 7.7 | 7.8 | 74.5762 | yes | 7
27 | 2.7 | 50 | 135 | 8.3 | 7.8 | 69.8996 | yes | 7
28 | 2.8 | 50 | 140 | 7.1 | 7.8 | 76.8126 | yes | 7
29 | 2.8 | 50 | 140 | 6.3 | 7.8 | 81.1771 | yes | 7
30 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012