## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-03-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.69 |  | 0.69
2 |  |  |  |  | 0.72 |  | 0.72
3 |  |  |  |  | 0.75 |  | 0.75
4 |  |  |  |  | 0.79 |  | 0.79
5 |  |  |  |  | 0.72 |  | 0.72
6 |  |  |  |  | 0.66 |  | 0.66
7 |  |  |  |  | 0.58 |  | 0.58
8 |  |  |  |  | 0.59 |  | 0.59
9 |  |  |  |  | 0.64 |  | 0.64
10 |  |  |  |  | 0.56 |  | 0.56
11 |  |  |  |  | 0.52 |  | 0.52
12 |  |  |  |  | 0.52 |  | 0.52
13 |  |  |  |  | 0.88 |  | 0.88
14 |  |  |  |  | 0.94 |  | 0.94
15 |  |  |  |  | 0.9 |  | 0.9
16 |  |  |  |  | 0.92 |  | 0.92
17 |  |  |  |  | 0.88 |  | 0.88
18 |  |  |  |  | 0.78 |  | 0.78
19 |  |  |  |  | 0.72 |  | 0.72
20 |  |  |  |  | 0.68 |  | 0.68
21 |  |  |  |  | 0.59 |  | 0.59
22 |  |  |  |  | 0.56 |  | 0.56
23 |  |  |  |  | 0.67 |  | 0.67
24 |  |  |  |  | 0.54 |  | 0.54
25 |  |  |  |  | 0.55 |  | 0.55
26 |  |  |  |  | 0.47 |  | 0.47
27 |  |  |  |  | 0.43 |  | 0.43
28 |  |  |  |  | 0.53 |  | 0.53
29 |  |  |  |  | 0.58 |  | 0.58
30 |  |  |  |  | 0.63 |  | 0.63
31 |  |  |  |  | 0.58 |  | 0.58
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 4/1/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.4 | 50 | 120 | 4.1 | 7.8 | 90.175 | yes | 7
2 | 2.5 | 50 | 125 | 5 | 7.8 | 85.7226 | yes | 7
3 | 2.2 | 50 | 110 | 4.4 | 7.8 | 86.2376 | yes | 7
4 | 2 | 50 | 100 | 3.7 | 7.8 | 88.4059 | yes | 7
5 | 2.2 | 50 | 110 | 5.2 | 7.8 | 81.586 | yes | 7
6 | 2.1 | 50 | 105 | 3.5 | 7.8 | 90.7181 | yes | 7
7 | 2.9 | 50 | 145 | 8.7 | 7.7 | 67.1297 | yes | 7
8 | 2.8 | 50 | 140 | 4.3 | 7.8 | 93.2716 | yes | 7
9 | 2.9 | 50 | 145 | 4.6 | 7.7 | 89.0735 | yes | 7
10 | 2.7 | 50 | 135 | 5.6 | 7.7 | 81.154 | yes | 7
11 | 2.7 | 50 | 135 | 6.2 | 7.8 | 80.7781 | yes | 7
12 | 2.6 | 50 | 130 | 5 | 7.8 | 86.7476 | yes | 7
13 | 2.8 | 50 | 140 | 6.5 | 7.8 | 80.062 | yes | 7
14 | 2.9 | 50 | 145 | 5 | 7.8 | 89.9004 | yes | 7
15 | 2.1 | 50 | 105 | 7.6 | 7.6 | 63.5502 | yes | 7
16 | 2 | 50 | 100 | 7.8 | 7.7 | 64.2542 | yes | 7
17 | 2.2 | 50 | 110 | 5.5 | 7.7 | 77.0233 | yes | 7
18 | 2.1 | 50 | 105 | 5.9 | 7.9 | 79.6989 | yes | 7
19 | 2.3 | 50 | 115 | 6.9 | 7.8 | 73.4182 | yes | 7
20 | 2.3 | 50 | 115 | 8.4 | 7.8 | 66.243 | yes | 7
21 | 2.1 | 50 | 105 | 9.6 | 7.8 | 59.64 | yes | 7
22 | 2.1 | 50 | 105 | 9.7 | 7.9 | 61.4186 | yes | 7
23 | 2.5 | 50 | 125 | 9 | 7.8 | 65.0882 | yes | 7
24 | 2.3 | 50 | 115 | 10.3 | 7.8 | 58.2127 | yes | 7
25 | 2.3 | 50 | 115 | 10.6 | 7.8 | 57.0435 | yes | 7
26 | 2.6 | 50 | 130 | 7.6 | 7.8 | 72.4837 | yes | 7
27 | 2.7 | 50 | 135 | 8.5 | 7.8 | 68.9479 | yes | 7
28 | 2.4 | 50 | 120 | 9.5 | 7.8 | 62.1784 | yes | 7
29 | 2.1 | 50 | 105 | 8.9 | 7.8 | 62.5446 | yes | 7
30 | 2.2 | 50 | 110 | 14.9 | 7.7 | 40.7182 | yes | 7
31 | 2.3 | 50 | 115 | 12.9 | 7.8 | 48.7705 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012