## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-04-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.77 |  | 0.77
2 |  |  |  |  | 0.68 |  | 0.68
3 |  |  |  |  | 0.56 |  | 0.56
4 |  |  |  |  | 0.47 |  | 0.47
5 |  |  |  |  | 0.41 |  | 0.41
6 |  |  |  |  | 0.32 |  | 0.32
7 |  |  |  |  | 0.3 |  | 0.3
8 |  |  |  |  | 0.39 |  | 0.39
9 |  |  |  |  | 0.33 |  | 0.33
10 |  |  |  |  | 0.36 |  | 0.36
11 |  |  |  |  | 0.34 |  | 0.34
12 |  |  |  |  | 0.35 |  | 0.35
13 |  |  |  |  | 0.34 |  | 0.34
14 |  |  |  |  | 0.36 |  | 0.36
15 |  |  |  |  | 0.35 |  | 0.35
16 |  |  |  |  | 0.3 |  | 0.3
17 |  |  |  |  | 0.28 |  | 0.28
18 |  |  |  |  | 0.27 |  | 0.27
19 |  |  |  |  | 0.34 |  | 0.34
20 |  |  |  |  | 0.27 |  | 0.27
21 |  |  |  |  | 0.27 |  | 0.27
22 |  |  |  |  | 0.3 |  | 0.3
23 |  |  |  |  | 0.28 |  | 0.28
24 |  |  |  |  | 0.32 |  | 0.32
25 |  |  |  |  | 0.33 |  | 0.33
26 |  |  |  |  | 0.35 |  | 0.35
27 |  |  |  |  | 0.32 |  | 0.32
28 |  |  |  |  | 0.3 |  | 0.3
29 |  |  |  |  | 0.28 |  | 0.28
30 |  |  |  |  | 0.25 |  | 0.25
31 |  |  |  |  | 0 |  | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 4/2/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 50 | 110 | 8.8 | 7.8 | 63.7105 | yes | 7
2 | 2.3 | 50 | 115 | 9.1 | 7.8 | 63.1541 | yes | 7
3 | 2.1 | 50 | 105 | 8.5 | 7.8 | 64.2722 | yes | 7
4 | 2.6 | 50 | 130 | 7.4 | 7.8 | 73.4874 | yes | 7
5 | 2.3 | 50 | 115 | 10.3 | 7.7 | 56.1534 | yes | 7
6 | 2.7 | 50 | 135 | 9.2 | 7.7 | 63.3784 | yes | 7
7 | 2.9 | 50 | 145 | 7.9 | 7.7 | 70.912 | yes | 7
8 | 2.5 | 50 | 125 | 6.7 | 7.8 | 76.2127 | yes | 7
9 | 2.8 | 50 | 140 | 12.5 | 7.4 | 45.7475 | yes | 7
10 | 2.6 | 50 | 130 | 5.9 | 7.6 | 75.7178 | yes | 7
11 | 2.6 | 50 | 130 | 8.6 | 7.7 | 65.2588 | yes | 7
12 | 2.7 | 50 | 135 | 9.4 | 7.7 | 62.5213 | yes | 7
13 | 2.5 | 50 | 125 | 10.4 | 7.8 | 59.1765 | yes | 7
14 | 2.7 | 50 | 135 | 10.2 | 7.8 | 61.3957 | yes | 7
15 | 2.6 | 50 | 130 | 9.4 | 7.8 | 64.0804 | yes | 7
16 | 2.7 | 50 | 135 | 9.9 | 7.7 | 60.4323 | yes | 7
17 | 2.7 | 50 | 135 | 4.9 | 7.8 | 88.3975 | yes | 7
18 | 2.8 | 50 | 140 | 17.7 | 7.6 | 34.8792 | yes | 7
19 | 2.5 | 50 | 125 | 16.7 | 7.6 | 36.0289 | yes | 7
20 | 2.5 | 50 | 125 | 13.7 | 7.7 | 45.6081 | yes | 7
21 | 2.7 | 50 | 135 | 7.4 | 7.7 | 71.6831 | yes | 7
22 | 2.6 | 50 | 130 | 9.4 | 7.7 | 61.7972 | yes | 7
23 | 2.7 | 50 | 135 | 11.4 | 7.7 | 54.6039 | yes | 7
24 | 2.7 | 50 | 135 | 13.2 | 7.8 | 50.0207 | yes | 7
25 | 2.7 | 50 | 135 | 11.3 | 7.8 | 56.9854 | yes | 7
26 | 2.7 | 50 | 135 | 13.1 | 7.7 | 48.538 | yes | 7
27 | 2.7 | 50 | 135 | 11.3 | 7.7 | 54.973 | yes | 7
28 | 2.9 | 50 | 145 | 9.1 | 7.7 | 65.3198 | yes | 7
29 | 2.3 | 50 | 115 | 11.3 | 7.6 | 50.6573 | yes | 7
30 | 2.3 | 50 | 115 | 11.2 | 7.7 | 52.8522 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012