## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-06-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.38 |  | 0.38
2 |  |  |  |  | 0.36 |  | 0.36
3 |  |  |  |  | 0.53 |  | 0.53
4 |  |  |  |  | 0.59 |  | 0.59
5 |  |  |  |  | 0.51 |  | 0.51
6 |  |  |  |  | 0.46 |  | 0.46
7 |  |  |  |  | 0.34 |  | 0.34
8 |  |  |  |  | 0.38 |  | 0.38
9 |  |  |  |  | 0.3 |  | 0.3
10 |  |  |  |  | 0.24 |  | 0.24
11 |  |  |  |  | 0.38 |  | 0.38
12 |  |  |  |  | 0.35 |  | 0.35
13 |  |  |  |  | 0.32 |  | 0.32
14 |  |  |  |  | 0.41 |  | 0.41
15 |  |  |  |  | 0.28 |  | 0.28
16 |  |  |  |  | 0.34 |  | 0.34
17 |  |  |  |  | 0.32 |  | 0.32
18 |  |  |  |  | 0.21 |  | 0.21
19 |  |  |  |  | 0.26 |  | 0.26
20 |  |  |  |  | 0.23 |  | 0.23
21 |  |  |  |  | 0.66 |  | 0.66
22 |  |  |  |  | 0.48 |  | 0.48
23 |  |  |  |  | 0.52 |  | 0.52
24 |  |  |  |  | 0.54 |  | 0.54
25 |  |  |  |  | 0.24 |  | 0.24
26 |  |  |  |  | 0.24 |  | 0.24
27 |  |  |  |  | 0.23 |  | 0.23
28 |  |  |  |  | 0.23 |  | 0.23
29 |  |  |  |  | 0.21 |  | 0.21
30 |  |  |  |  | 0.24 |  | 0.24
31 |  |  |  |  | 0 |  | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 7/3/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.7 | 50 | 135 | 16.2 | 7.7 | 39.531 | yes | 7
2 | 2.7 | 50 | 135 | 15.9 | 7.7 | 40.3255 | yes | 7
3 | 2.8 | 50 | 140 | 15.3 | 7.9 | 45.6778 | yes | 7
4 | 2.3 | 50 | 115 | 13.3 | 7.8 | 47.4978 | yes | 7
5 | 2.2 | 50 | 110 | 17.9 | 7.7 | 33.3597 | yes | 7
6 | 2.4 | 50 | 120 | 18.8 | 7.7 | 32.1414 | yes | 7
7 | 2.3 | 50 | 115 | 20.1 | 7.7 | 29.1366 | yes | 7
8 | 2.3 | 50 | 115 | 20.6 | 7.7 | 28.1788 | yes | 7
9 | 2.2 | 50 | 110 | 20.4 | 7.7 | 28.2339 | yes | 7
10 | 2.4 | 50 | 120 | 21.2 | 7.7 | 27.381 | yes | 7
11 | 2.6 | 50 | 130 | 18.7 | 7.7 | 33.101 | yes | 7
12 | 2.5 | 50 | 125 | 20.9 | 7.6 | 27.2263 | yes | 7
13 | 2.4 | 50 | 120 | 19.9 | 7.7 | 29.8672 | yes | 7
14 | 2.7 | 50 | 135 | 17.1 | 7.7 | 37.2384 | yes | 7
15 | 2.6 | 50 | 130 | 16.1 | 7.7 | 39.3458 | yes | 7
16 | 2.7 | 50 | 135 | 13.2 | 7.8 | 50.0207 | yes | 7
17 | 2.7 | 50 | 135 | 11.8 | 7.9 | 57.1122 | yes | 7
18 | 2.6 | 50 | 130 | 13.4 | 7.7 | 47.0506 | yes | 7
19 | 2.8 | 50 | 140 | 20.4 | 7.7 | 30.2345 | yes | 7
20 | 3 | 50 | 150 | 21.3 | 7.7 | 29.1276 | yes | 7
21 | 2.9 | 50 | 145 | 17.2 | 7.6 | 36.47 | yes | 7
22 | 2.4 | 50 | 120 | 16.8 | 7.7 | 36.7169 | yes | 7
23 | 2.6 | 50 | 130 | 12.6 | 7.7 | 49.6055 | yes | 7
24 | 3 | 50 | 150 | 14.4 | 7.7 | 46.0746 | yes | 7
25 | 3 | 50 | 150 | 20.6 | 7.7 | 30.5215 | yes | 7
26 | 2.3 | 50 | 115 | 16 | 7.8 | 39.7211 | yes | 7
27 | 2.1 | 50 | 105 | 16.8 | 7.9 | 38.2057 | yes | 7
28 | 2.3 | 50 | 115 | 18.6 | 7.9 | 34.6763 | yes | 7
29 | 2.3 | 50 | 115 | 17.9 | 8 | 37.694 | yes | 7
30 | 3 | 50 | 150 | 18.8 | 7.9 | 37.0486 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012