## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-08-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.21 |  | 0.21
2 |  |  |  |  | 0.2 |  | 0.2
3 |  |  |  |  | 0.26 |  | 0.26
4 |  |  |  |  | 0.28 |  | 0.28
5 |  |  |  |  | 0.27 |  | 0.27
6 |  |  |  |  | 0.33 |  | 0.33
7 |  |  |  |  | 0.27 |  | 0.27
8 |  |  |  |  | 0.25 |  | 0.25
9 |  |  |  |  | 0.26 |  | 0.26
10 |  |  |  |  | 0.27 |  | 0.27
11 |  |  |  |  | 0.33 |  | 0.33
12 |  |  |  |  | 0.35 |  | 0.35
13 |  |  |  |  | 0.27 |  | 0.27
14 |  |  |  |  | 0.38 |  | 0.38
15 |  |  |  |  | 0.27 |  | 0.27
16 |  |  |  |  | 0.29 |  | 0.29
17 |  |  |  |  | 0.3 |  | 0.3
18 |  |  |  |  | 0.25 |  | 0.25
19 |  |  |  |  | 0.32 |  | 0.32
20 |  |  |  |  | 0.25 |  | 0.25
21 |  |  |  |  | 0.29 |  | 0.29
22 |  |  |  |  | 0.29 |  | 0.29
23 |  |  |  |  | 0.21 |  | 0.21
24 |  |  |  |  | 0.2 |  | 0.2
25 |  |  |  |  | 0.26 |  | 0.26
26 |  |  |  |  | 0.28 |  | 0.28
27 |  |  |  |  | 0.25 |  | 0.25
28 |  |  |  |  | 0.22 |  | 0.22
29 |  |  |  |  | 0.33 |  | 0.33
30 |  |  |  |  | 0.25 |  | 0.25
31 |  |  |  |  | 0.3 |  | 0.3
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 9/1/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3 | 50 | 150 | 20.5 | 8.1 | 35.6258 | yes | 7
2 | 3 | 50 | 150 | 21.9 | 8.1 | 32.456 | yes | 7
3 | 2.5 | 50 | 125 | 23 | 8.1 | 28.4877 | yes | 7
4 | 2.7 | 50 | 135 | 21.6 | 8 | 30.8365 | yes | 7
5 | 2.9 | 50 | 145 | 20.7 | 8 | 33.4967 | yes | 7
6 | 2.7 | 50 | 135 | 19 | 8 | 36.6643 | yes | 7
7 | 2.9 | 50 | 145 | 18.9 | 8.1 | 39.1735 | yes | 7
8 | 2.4 | 50 | 120 | 22.5 | 8.1 | 29.1216 | yes | 7
9 | 2.5 | 50 | 125 | 21.6 | 8.1 | 31.2795 | yes | 7
10 | 2.1 | 50 | 105 | 22.6 | 8.1 | 27.9535 | yes | 7
11 | 2.7 | 50 | 135 | 21.6 | 8.1 | 32 | yes | 7
12 | 2.2 | 50 | 110 | 19 | 8 | 34.6408 | yes | 7
13 | 2.4 | 50 | 120 | 19.1 | 8.1 | 36.5259 | yes | 7
14 | 2.4 | 50 | 120 | 19.1 | 8 | 35.2019 | yes | 7
15 | 2.3 | 50 | 115 | 18.9 | 8.2 | 37.9722 | yes | 7
16 | 2.2 | 50 | 110 | 17 | 8.1 | 41.0476 | yes | 7
17 | 2.7 | 50 | 135 | 16.7 | 8.2 | 45.9669 | yes | 7
18 | 2.3 | 50 | 115 | 19.1 | 8.1 | 36.1137 | yes | 7
19 | 2.1 | 50 | 105 | 16.6 | 7.9 | 38.7163 | yes | 7
20 | 2 | 50 | 100 | 18.2 | 8 | 35.7134 | yes | 7
21 | 2 | 50 | 100 | 18.5 | 8 | 35.0079 | yes | 7
22 | 2.5 | 50 | 125 | 17.3 | 8.1 | 41.6294 | yes | 7
23 | 2 | 50 | 100 | 16.8 | 8 | 39.1935 | yes | 7
24 | 2 | 50 | 100 | 13.4 | 8.1 | 50.9233 | yes | 7
25 | 2.1 | 50 | 105 | 14 | 8.1 | 49.4998 | yes | 7
26 | 2.2 | 50 | 110 | 14.8 | 8.1 | 47.4834 | yes | 7
27 | 2 | 50 | 100 | 18.9 | 8 | 34.0885 | yes | 7
28 | 2.3 | 50 | 115 | 16 | 8 | 42.7561 | yes | 7
29 | 2.4 | 50 | 120 | 24.5 | 8 | 24.54 | yes | 7
30 | 2.3 | 50 | 115 | 18.5 | 8 | 36.221 | yes | 7
31 | 2.7 | 50 | 135 | 15.9 | 8 | 45.0314 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012