## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-09-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.15 |  | 0.15
2 |  |  |  |  | 0.26 |  | 0.26
3 |  |  |  |  | 0.22 |  | 0.22
4 |  |  |  |  | 0.29 |  | 0.29
5 |  |  |  |  | 0.34 |  | 0.34
6 |  |  |  |  | 0.22 |  | 0.22
7 |  |  |  |  | 0.23 |  | 0.23
8 |  |  |  |  | 0.21 |  | 0.21
9 |  |  |  |  | 0.22 |  | 0.22
10 |  |  |  |  | 0.18 |  | 0.18
11 |  |  |  |  | 0.34 |  | 0.34
12 |  |  |  |  | 0.26 |  | 0.26
13 |  |  |  |  | 0.27 |  | 0.27
14 |  |  |  |  | 0.22 |  | 0.22
15 |  |  |  |  | 0.19 |  | 0.19
16 |  |  |  |  | 0.19 |  | 0.19
17 |  |  |  |  | 0.21 |  | 0.21
18 |  |  |  |  | 0.41 |  | 0.41
19 |  |  |  |  | 0.27 |  | 0.27
20 |  |  |  |  | 0.26 |  | 0.26
21 |  |  |  |  | 0.22 |  | 0.22
22 |  |  |  |  | 0.31 |  | 0.31
23 |  |  |  |  | 0.31 |  | 0.31
24 |  |  |  |  | 0.16 |  | 0.16
25 |  |  |  |  | 0.24 |  | 0.24
26 |  |  |  |  | 0.2 |  | 0.2
27 |  |  |  |  | 0.22 |  | 0.22
28 |  |  |  |  | 0.21 |  | 0.21
29 |  |  |  |  | 0.19 |  | 0.19
30 |  |  |  |  | 0.17 |  | 0.17
31 |  |  |  |  | 0 |  | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 10/1/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.2 | 50 | 160 | 17.2 | 8.1 | 45.358 | yes | 7
2 | 2.6 | 50 | 130 | 17.8 | 8 | 39.2576 | yes | 7
3 | 2 | 50 | 100 | 16.8 | 8.2 | 42.189 | yes | 7
4 | 2.2 | 50 | 110 | 18.9 | 8 | 34.8721 | yes | 7
5 | 2.2 | 50 | 110 | 19.8 | 8 | 32.8442 | yes | 7
6 | 2 | 50 | 100 | 21.9 | 8.1 | 28.9604 | yes | 7
7 | 2.1 | 50 | 105 | 18.8 | 8 | 34.7083 | yes | 7
8 | 2.6 | 50 | 130 | 18.4 | 8 | 37.7248 | yes | 7
9 | 2.8 | 50 | 140 | 18.5 | 8.3 | 42.8128 | yes | 7
10 | 2.5 | 50 | 125 | 16.2 | 8.3 | 48.1888 | yes | 7
11 | 2.4 | 50 | 120 | 16.7 | 8.2 | 44.4347 | yes | 7
12 | 2.2 | 50 | 110 | 15.9 | 8.2 | 45.8035 | yes | 7
13 | 2 | 50 | 100 | 13.6 | 8.1 | 50.2551 | yes | 7
14 | 2.7 | 50 | 135 | 15.2 | 8.1 | 48.9294 | yes | 7
15 | 2.8 | 50 | 140 | 15.5 | 8 | 46.7643 | yes | 7
16 | 2.4 | 50 | 120 | 11.5 | 8.1 | 60.5054 | yes | 7
17 | 2.6 | 50 | 130 | 13.5 | 8.1 | 54.1282 | yes | 7
18 | 2.7 | 50 | 135 | 14.9 | 8.1 | 49.909 | yes | 7
19 | 2.7 | 50 | 135 | 14.6 | 8.1 | 50.9078 | yes | 7
20 | 3 | 50 | 150 | 13.3 | 8.1 | 57.3743 | yes | 7
21 | 2.6 | 50 | 130 | 13.7 | 8.1 | 53.4186 | yes | 7
22 | 2.8 | 50 | 140 | 14.5 | 8.1 | 51.8262 | yes | 7
23 | 2.8 | 50 | 140 | 14.8 | 8.1 | 50.8096 | yes | 7
24 | 2.8 | 50 | 140 | 15 | 8.1 | 50.1428 | yes | 7
25 | 3.1 | 50 | 155 | 16.1 | 8.1 | 48.2329 | yes | 7
26 | 2.5 | 50 | 125 | 14.7 | 8.1 | 49.4444 | yes | 7
27 | 2.6 | 50 | 130 | 15.6 | 8.1 | 47.1177 | yes | 7
28 | 2.6 | 50 | 130 | 13.8 | 8.1 | 53.0672 | yes | 7
29 | 2.3 | 50 | 115 | 17.6 | 8 | 38.4523 | yes | 7
30 | 2.1 | 50 | 105 | 18.9 | 8 | 34.4781 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012