## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-10-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.18 |  | 0.18
2 |  |  |  |  | 0.25 |  | 0.25
3 |  |  |  |  | 0.21 |  | 0.21
4 |  |  |  |  | 0.21 |  | 0.21
5 |  |  |  |  | 0.24 |  | 0.24
6 |  |  |  |  | 0.22 |  | 0.22
7 |  |  |  |  | 0.22 |  | 0.22
8 |  |  |  |  | 0.21 |  | 0.21
9 |  |  |  |  | 0.26 |  | 0.26
10 |  |  |  |  | 0.21 |  | 0.21
11 |  |  |  |  | 0.24 |  | 0.24
12 |  |  |  |  | 0.28 |  | 0.28
13 |  |  |  |  | 0.28 |  | 0.28
14 |  |  |  |  | 0.26 |  | 0.26
15 |  |  |  |  | 0.17 |  | 0.17
16 |  |  |  |  | 0.26 |  | 0.26
17 |  |  |  |  | 0.31 |  | 0.31
18 |  |  |  |  | 0.23 |  | 0.23
19 |  |  |  |  | 0.21 |  | 0.21
20 |  |  |  |  | 0.25 |  | 0.25
21 |  |  |  |  | 0.29 |  | 0.29
22 |  |  |  |  | 0.22 |  | 0.22
23 |  |  |  |  | 0.33 |  | 0.33
24 |  |  |  |  | 0.17 |  | 0.17
25 |  |  |  |  | 0.27 |  | 0.27
26 |  |  |  |  | 0.22 |  | 0.22
27 |  |  |  |  | 0.24 |  | 0.24
28 |  |  |  |  | 0.26 |  | 0.26
29 |  |  |  |  | 0.29 |  | 0.29
30 |  |  |  |  | 0.22 |  | 0.22
31 |  |  |  |  | 0.31 |  | 0.31
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 11/02/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 50 | 110 | 19.2 | 8.1 | 35.4694 | yes | 7
2 | 2.7 | 50 | 135 | 15.2 | 8 | 47.1656 | yes | 7
3 | 2.8 | 50 | 140 | 12 | 8 | 59.0942 | yes | 7
4 | 2.8 | 50 | 140 | 10.1 | 8 | 67.2556 | yes | 7
5 | 2.6 | 50 | 130 | 11.3 | 8 | 60.5448 | yes | 7
6 | 2.4 | 50 | 120 | 10.9 | 8.1 | 63.0246 | yes | 7
7 | 2 | 50 | 100 | 10.2 | 8.1 | 63.0894 | yes | 7
8 | 2.4 | 50 | 120 | 11.8 | 8.1 | 59.2865 | yes | 7
9 | 2.2 | 50 | 110 | 17.1 | 8 | 39.3017 | yes | 7
10 | 2.3 | 50 | 115 | 9.5 | 8 | 66.0882 | yes | 7
11 | 2.2 | 50 | 110 | 13.7 | 8 | 49.2238 | yes | 7
12 | 2.2 | 50 | 110 | 9.1 | 8 | 67.1297 | yes | 7
13 | 2.3 | 50 | 115 | 11.6 | 8 | 57.2976 | yes | 7
14 | 2.4 | 50 | 120 | 10.1 | 8 | 64.1822 | yes | 7
15 | 2.2 | 50 | 110 | 15.8 | 7.4 | 34.3372 | yes | 7
16 | 2.1 | 50 | 105 | 14.2 | 7.7 | 42.1719 | yes | 7
17 | 2.1 | 50 | 105 | 11.8 | 7.7 | 49.62 | yes | 7
18 | 2.5 | 50 | 125 | 10 | 7.9 | 63.0482 | yes | 7
19 | 2 | 50 | 100 | 15.1 | 7.7 | 39.2816 | yes | 7
20 | 2.1 | 50 | 105 | 12.2 | 7.7 | 48.314 | yes | 7
21 | 2 | 50 | 100 | 10.8 | 7.7 | 52.4504 | yes | 7
22 | 1.9 | 50 | 95 | 12.8 | 7.7 | 45.2335 | yes | 7
23 | 2 | 50 | 100 | 8.5 | 7.7 | 61.2644 | yes | 7
24 | 2 | 50 | 100 | 9.5 | 7.7 | 57.2498 | yes | 7
25 | 2.1 | 50 | 105 | 8.8 | 7.7 | 60.7309 | yes | 7
26 | 2.2 | 50 | 110 | 9.4 | 7.7 | 58.9901 | yes | 7
27 | 2.2 | 50 | 110 | 9.4 | 7.7 | 58.9901 | yes | 7
28 | 2.1 | 50 | 105 | 9.6 | 7.7 | 57.5262 | yes | 7
29 | 1.9 | 50 | 95 | 9.3 | 7.9 | 61.6593 | yes | 7
30 | 2 | 50 | 100 | 7.8 | 7.7 | 64.2542 | yes | 7
31 | 2.3 | 50 | 115 | 8.5 | 7.7 | 63.4435 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012