## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-11-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.26 |  | 0.26
2 |  |  |  |  | 0.24 |  | 0.24
3 |  |  |  |  | 0.23 |  | 0.23
4 |  |  |  |  | 0.21 |  | 0.21
5 |  |  |  |  | 0.3 |  | 0.3
6 |  |  |  |  | 0.23 |  | 0.23
7 |  |  |  |  | 0.26 |  | 0.26
8 |  |  |  |  | 0.21 |  | 0.21
9 |  |  |  |  | 0.24 |  | 0.24
10 |  |  |  |  | 0.24 |  | 0.24
11 |  |  |  |  | 0.25 |  | 0.25
12 |  |  |  |  | 0.18 |  | 0.18
13 |  |  |  |  | 0.2 |  | 0.2
14 |  |  |  |  | 0.22 |  | 0.22
15 |  |  |  |  | 0.21 |  | 0.21
16 |  |  |  |  | 0.25 |  | 0.25
17 |  |  |  |  | 0.26 |  | 0.26
18 |  |  |  |  | 0.25 |  | 0.25
19 |  |  |  |  | 0.26 |  | 0.26
20 |  |  |  |  | 0.29 |  | 0.29
21 |  |  |  |  | 0.32 |  | 0.32
22 |  |  |  |  | 0.39 |  | 0.39
23 |  |  |  |  | 0.38 |  | 0.38
24 |  |  |  |  | 0.4 |  | 0.4
25 |  |  |  |  | 0.38 |  | 0.38
26 |  |  |  |  | 0.36 |  | 0.36
27 |  |  |  |  | 0.37 |  | 0.37
28 |  |  |  |  | 0.37 |  | 0.37
29 |  |  |  |  | 0.39 |  | 0.39
30 |  |  |  |  | 0.29 |  | 0.29
31 |  |  |  |  | 0 |  | 0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 12/02/2024
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 50 | 100 | 9.2 | 7.7 | 58.4236 | yes | 7
2 | 2.1 | 50 | 105 | 8.3 | 7.7 | 62.831 | yes | 7
3 | 2.2 | 50 | 110 | 8.4 | 7.7 | 63.1365 | yes | 7
4 | 2.1 | 50 | 105 | 8.7 | 7.7 | 61.1448 | yes | 7
5 | 2.3 | 50 | 115 | 9.1 | 7.7 | 60.9063 | yes | 7
6 | 2.9 | 50 | 145 | 10.5 | 7.6 | 57.2816 | yes | 7
7 | 2 | 50 | 100 | 11.5 | 7.6 | 48.3008 | yes | 7
8 | 2.7 | 50 | 135 | 7.4 | 7.6 | 69.1099 | yes | 7
9 | 2.5 | 50 | 125 | 8.2 | 7.6 | 63.9191 | yes | 7
10 | 2.9 | 50 | 145 | 8.6 | 7.7 | 67.5905 | yes | 7
11 | 2.9 | 50 | 145 | 8.6 | 7.7 | 67.5905 | yes | 7
12 | 2.9 | 50 | 145 | 8 | 7.7 | 70.427 | yes | 7
13 | 2.7 | 50 | 135 | 9 | 7.7 | 64.2482 | yes | 7
14 | 2.7 | 50 | 135 | 9.7 | 7.7 | 61.2587 | yes | 7
15 | 2.6 | 50 | 130 | 8.3 | 7.7 | 66.6099 | yes | 7
16 | 2 | 50 | 100 | 6.9 | 7.7 | 68.3297 | yes | 7
17 | 2.3 | 50 | 115 | 6.6 | 7.7 | 72.2521 | yes | 7
18 | 2.7 | 50 | 135 | 5.6 | 7.8 | 84.205 | yes | 7
19 | 2.6 | 50 | 130 | 5.1 | 7.7 | 83.0223 | yes | 7
20 | 2.2 | 50 | 110 | 7.7 | 7.6 | 63.8594 | yes | 7
21 | 2.6 | 50 | 130 | 7.7 | 7.6 | 66.9163 | yes | 7
22 | 2.7 | 50 | 135 | 8.7 | 7.6 | 63.2367 | yes | 7
23 | 2.9 | 50 | 145 | 8.3 | 7.6 | 66.5226 | yes | 7
24 | 2.8 | 50 | 140 | 7.8 | 7.6 | 68.0355 | yes | 7
25 | 3 | 50 | 150 | 7.6 | 7.6 | 70.6126 | yes | 7
26 | 2.6 | 50 | 130 | 8 | 7.5 | 63.219 | yes | 7
27 | 3 | 50 | 150 | 8.9 | 7.5 | 62.3002 | yes | 7
28 | 3 | 50 | 150 | 7.8 | 7.5 | 67.1549 | yes | 7
29 | 2.9 | 50 | 145 | 5.7 | 7.5 | 76.6676 | yes | 7
30 | 3 | 50 | 150 | 6 | 7.5 | 75.9899 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012